## Pros.Cons
| Pros | Cons
Laudry Dryer Exhaust | Exhaust temperature and flow rate fairly consistent | Dryer lint would clog conventional heat exchangers
| Dryers used continuously throughout YMCA operating hours | Significant temperature drop would cause condensation in exhaust tube
Air contains significantly less heat than water (Hard numbers?)
Laundry Graywater | Wastewater contains a significant amount of energy (washers use hot water for wash and rinse, no cold water added) | To be effective, wastewater heat exchangers require a vertical drop or pool of water – laundry room in basement, slab-on-grade
Wastewater is discharged intermittently
Showers - Basement | Largest source of graywater at YMCA | Lockerrooms in basement, slab-on-grade. Drains pass through slab.
| Regular flow | Multiple locations might require multiple exchangers
Use coincides with flow
Showers - Residential and Women's Fitness Center | Showers are on second through fourth floor -- opportunity for a vertical drop exchanger | Shower use may be asymetric throughout day, most showers in the morning.
All wastewater passes through one drain.
Sumptank Graywater | All wastewater passes through two sump tanks | Hot wastewater mixed with cold, reducing Δt and efficiency of heat exchanger
| Sump tanks are adjacent to pool heaters and boilers. | Wastewater passes through concrete slab – losing some heat to the ground
| Tank of water overcomes need for vertical drop in graywater | All solid and noxious waste passes through sump tanks
Continuous flow

## Recovery Compared
| Actual Recovery | Consumption Avoided
Basement Showers | 8423.1 | 12033 | Therms | 11070.36
Residential/ Women's Fitness Showers | 5054 | 7220 |  | 6642.4
Laundry Dryers | 2958.2 | 4226 |  | 3887.92
Laundry Washers | 884.8 | 1264 |  | 1162.88
| Current energy use | Net use with heat recovery system |  | Therms Avoided
Basement Showers | 29299 | 17266 | Therms | 12033
Residential/ Women's Fitness Showers | 14650 | 7430 |  | 7220
Laundry Dryers | 21024 | 16798 |  | 4226
Laundry Washers | 3515 | 2141 |  | 1374
$35,700
$18,750
$29,910
$4,500
$15,400
$9,240
$5,410
$1,759
Annual Savings:
$15,400
$9,240
$5,410
$1,760

## Shower Energy Use
Shower Energy Use and Potential Recovery
| Basement Locker Rooms | Women's Fitness Center |  | Residential
Cold Water Temperature | 54 | 54 |  | 54 | oF
Hot Water (boiler) | 140 | 140 |  | 140 | oF
Temperature of Shower1 | 110 | 110 |  | 110 | oF
Hot water/Total flow of shower | 0.65116 | 0.65116 |  | 0.65116
Efficiency of Boiler/hot water pipes | 70 | 70 |  | 70 | %
Thermal capacity of water | 62.4 | 62.4 |  | 62.4 | Btu/ft3 of
Gallons to Ft3 Conversion | 0.134 | 0.134 |  | 0.134 | gallons/ft3
Energy to heat one gallon of shower water | 668.928 | 668.928 |  | 668.928 | Btus/gallon
Shower flow rate (GPM)2 | 2.5 | 2.5 |  | 2.5 | gallons/minute
Average length of shower3 | 4 | 4 |  | 12 | minutes
Estimated Number of showers4, 5 | 1200 | 300 |  | 100 | showers/day
Daily shower water usage | 12000 | 3000 |  | 3000 | gallons/day
Energy used to heat shower water | 8027136 | 2006784 |  | 2006784 | Btus/day
Therms used per day (100,000 Btu) | 80.2714 | 20.0678 |  | 20.0678 | Therms/day
Therms used per year | 29299.0464 | 7324.7616 | 0 | 7324.7616 | Therms/year
Cost of one therm (YMCA bill, Jan. 2001) | 1.28 | 1.28 |  | 1.28
Estimated cost of heating shower water | 102.7473 | 25.6868 |  | 25.6868 | per day
| 37502.7794 | 9375.6948 |  | 9375.6948 | per year
1Temperature of shower is based on national average, ASHRAE Applications Handbook, 1995
2Designated installation
3Estimated, based on national averages
4The estimates for the total number of showers daily are based on towel usage (3,000 to 5,000 daily) and interviews with Fran Gallati and Neal Henderson.
5Showers are divided by lockerroom as follows. The majority of showers are taken by adults in the men's, women's, and women's fitness center locker rooms. 2/3 of the Y members are women, but the majority use the basement locker room (which is adjacent to the pool). It is estimated that only 1/3 of women take their showers in the women's fitness center. This means about 20% of all showers taken at the Y are taken in the women's fitness center, while the rest are taken in the basement locker rooms.

## Laundry Washer Energy Use
Laundry Washing Machine Energy Use and Potential Recovery
| # | Unit
Cold water temperature | 54 | oF
Hot water entering washer | 140 | oF
Temperature change | 86 | oF
Efficiency of Boiler/hot water pipes | 70 | %
Thermal capacity of water | 62.4 | Btu/ft3 of
Gallons to Ft3 Conversion | 0.134 | gallons/ft3
Energy to heat one gallon of laundry water | 1027.2823 | Btu/gallon
Hot water use per load of wash1 | 15 | gallons/cycle
Towels washed per day | 5000 | towels
# of cycles per day (80 towels a cycle) | 62.5 | cycles
Daily laundry water usage | 937.5 | gallons/day
Energy used to heat laundry water | 963077.1429 | Btus/day
Therms used per day (100,000 Btu) | 9.6308 | therms/day
Therms used per year | 3515.2316 | therms/year
Cost of one therm (YMCA bill, Jan. 2001) | 1.28
Estimated cost of heating laundry water | 12.3274 | per day
| 4499.4964 | per year
1 Manufacturer's specifications: 10-19 gallons per cycle

## Greywater Heat Recovery
Potential Greywater Heat Recovery
| Basement Locker Room Showers | Women's Fitness Center and Residential Showers | Laundry Washing Machines
Energy Usage | 80.2714 | 40.2 | 9.6 | Therms/day
| 29299.0464 | 14673 | 3504 | Therms/year
Daily Flow | 12000 | 6000 | 938 | gallons/day
Temperature of water reaching drain | 100 | 100 | 110
Cold Water Temp | 54 | 54 | 54
Efficiency of Exchanger1 | 50 | 60 | 60 | %
Actual Therms recovered | 23.078 | 13.8468 | 2.6353 | therms/day
| 8423.4758 | 5054.0855 | 961.8877 | therms/year
Annual energy consumption avoided2 | 12033.5369 | 7220.1221 | 1374.1253 | therms/year
Annual energy costs avoided2 | 15402.9273 | 9241.7564 | 1758.8804 | per year
1Efficicency of recovering heat from sump tanks is estimated at 50% for a home built system. This efficiency is used for all greywater sources in the basement. Where a vertical drain heat recovery system could be used (I.e. any greywater source on the first floor or above), 60% efficiency is used. This is the observed efficiency for the GFX heat exchanger, model GS-60.
2Takes into account efficiency of boiler (70%). Because the boilers use 1.4 therms of energy to heat a volume of water by one therm, for each therm we heat the water, we avoid buying 1.4 therms.

## Laundry Dryer Heat Recovery
Dryer Energy Use and Potential Recovery
Energy Use Estimate
Dryer BTU input1 | 180000 | BTUs/Hour
Number of dryers | 4 | Dryers
Laundry room hours of operation | 16 | Hours/Day
Percentage of time each dryer is running | 50 | %
Daily Energy Use | 5760000 | BTUs
| 57.6 | Therms/Day
Cost of one therm (YMCA bill, Jan. 2001) | 1.28 | US$
Projected cost of dryer use | 73.728 | per day
Estimated yearly expenditures | 21024 | Therms per year
| 26910.72 | per year
Recovery Estimate
Rate of exhaust | 1000 | CFM
Temperature of exhaust2 | 117 | oF
Average external air temperature | 50 | oF
Delta T (70% thermal effectiveness)3 | 46.9 | oF
Conversion factor4 | 1.08 | Btu-min/ft3 - oF-Hr
Heat recovery potential | 50652 | BTU/Hr
| 0.50652 | Therms/Hr
Laundry room hours of operation | 16 | Hours/Day
Annual recovery potential | 2958.0768 | Therms/Year
Annual energy consumption avoided5 | 4225.824 | Therms/Year
Cost of one therm | 1.28
Annual energy costs avoided5 | 5409.0547 | per year
1 Manufacturer's specification
2Average Hobo reading at roof exhaust pipe during hours of operation.
3Based on an estimate from Tim Tilley, Envirosep Corp.
4MEEB, page 300
5Takes into account efficiency of boiler (70%)

## Spot Measurements
Laundry Dryer Exhaust Tube
Exhaust | Temperature |  | Flow Rate
Spot measurements, 4 PM, 1/13/01 | 113 | oF | 930 | feet/minute
| 114 |  | 860
| 115 |  | 1080
| 122 |  | 440
Further measurements showed an average of about 1000 ft./min., with a peak of 1300 ft/min.
Tube Size
Exhaust tube diameter |  | 13.5 inches
Exhaust tube cross sectional area |  | 1 square foot
Exhaust Tube Surface | Temperature
Exhaust tube in laundry room | 130 | oF
Exhaust tube on roof | 77
13.5 inches

## Hobo Graphs
Saturday
Sunday
Friday
Saturday

## Sump Data
Date Time | Temperature (*F) | Date Time | Temperature (*F) -- Three point moving average
2001-02-17 16:38 | 85.28 | 36939.6981 | 83.85
2001-02-17 16:39 | 85.28 | 36939.6988 | 83.96
2001-02-17 16:40 | 84.95 | 36939.6995 | 84.18
2001-02-17 16:41 | 84.62 | 36939.7002 | 84.9567
2001-02-17 16:42 | 83.96 | 36939.7009 | 85.9567
2001-02-17 16:43 | 83.96 | 36939.7016 | 86.9633
2001-02-17 16:44 | 83.63 | 36939.7023 | 87.53
2001-02-17 16:45 | 83.96 | 36939.703 | 87.8733
2001-02-17 16:46 | 83.96 | 36939.7037 | 88.1033
2001-02-17 16:47 | 83.96 | 36939.7044 | 88.3333
2001-02-17 16:48 | 84.62 | 36939.7051 | 88.5633
2001-02-17 16:49 | 86.29 | 36939.7058 | 88.5633
2001-02-17 16:50 | 86.96 | 36939.7065 | 88.3333
2001-02-17 16:51 | 87.64 | 36939.7072 | 87.9867
2001-02-17 16:52 | 87.99 | 36939.7079 | 87.7567
2001-02-17 16:53 | 87.99 | 36939.7086 | 87.4133
2001-02-17 16:54 | 88.33 | 36939.7092 | 87.3
2001-02-17 16:55 | 88.68 | 36939.7099 | 87.1867
2001-02-17 16:56 | 88.68 | 36939.7106 | 87.1867
2001-02-17 16:57 | 88.33 | 36939.7113 | 87.0733
2001-02-17 16:58 | 87.99 | 36939.712 | 86.8467
2001-02-17 16:59 | 87.64 | 36939.7127 | 86.7333
2001-02-17 17:00 | 87.64 | 36939.7134 | 87.8867
2001-02-17 17:01 | 86.96 | 36939.7141 | 89.5033
2001-02-17 17:02 | 87.3 | 36939.7148 | 91.0033
2001-02-17 17:03 | 87.3 | 36939.7155 | 91.59
2001-02-17 17:04 | 86.96 | 36939.7162 | 91.59
2001-02-17 17:05 | 86.96 | 36939.7169 | 91.7067
2001-02-17 17:06 | 86.62 | 36939.7176 | 91.3533
2001-02-17 17:07 | 86.62 | 36939.7183 | 91.2367
2001-02-17 17:08 | 90.42 | 36939.719 | 91.0033
2001-02-17 17:09 | 91.47 | 36939.7197 | 90.6533
2001-02-17 17:10 | 91.12 | 36939.7204 | 89.9567
2001-02-17 17:11 | 92.18 | 36939.7211 | 89.03
2001-02-17 17:12 | 91.47 | 36939.7217 | 88.22
2001-02-17 17:13 | 91.47 | 36939.7224 | 87.4167
2001-02-17 17:14 | 91.12 | 36939.7231 | 86.2933
2001-02-17 17:15 | 91.12 | 36939.7238 | 84.8467
2001-02-17 17:16 | 90.77 | 36939.7245 | 83.41
2001-02-17 17:17 | 90.07 | 36939.7252 | 82.4233
2001-02-17 17:18 | 89.03 | 36939.7259 | 82.2033
2001-02-17 17:19 | 87.99 | 36939.7266 | 82.4233
2001-02-17 17:20 | 87.64 | 36939.7273 | 82.64
2001-02-17 17:21 | 86.62 | 36939.728 | 82.64
2001-02-17 17:22 | 84.62 | 36939.7287 | 82.53
2001-02-17 17:23 | 83.3 | 36939.7294 | 82.3133
2001-02-17 17:24 | 82.31 | 36939.7301 | 81.7733
2001-02-17 17:25 | 81.66 | 36939.7308 | 81.1267
2001-02-17 17:26 | 82.64 | 36939.7315 | 80.7
2001-02-17 17:27 | 82.97 | 36939.7322 | 80.4867
2001-02-17 17:28 | 82.31 | 36939.7329 | 80.38
2001-02-17 17:29 | 82.64 | 36939.7336 | 80.38
2001-02-17 17:30 | 82.64 | 36939.7342 | 80.4867
2001-02-17 17:31 | 81.66 | 36939.7349 | 80.7
2001-02-17 17:32 | 81.02 | 36939.7356 | 81.1267
2001-02-17 17:33 | 80.7 | 36939.7363 | 81.9933
2001-02-17 17:34 | 80.38 | 36939.737 | 83.0833
2001-02-17 17:35 | 80.38 | 36939.7377 | 84.18
2001-02-17 17:36 | 80.38 | 36939.7384 | 84.73
2001-02-17 17:37 | 80.38 | 36939.7391 | 84.95
2001-02-17 17:38 | 80.7 | 36939.7398 | 85.06
2001-02-17 17:39 | 81.02 | 36939.7405 | 85.17
2001-02-17 17:40 | 81.66 | 36939.7412 | 85.17
2001-02-17 17:41 | 83.3 | 36939.7419 | 85.2833
2001-02-17 17:42 | 84.29 | 36939.7426 | 85.62
2001-02-17 17:43 | 84.95 | 36939.7433 | 86.1767
2001-02-17 17:44 | 84.95 | 36939.744 | 86.51
2001-02-17 17:45 | 84.95 | 36939.7447 | 86.3967
2001-02-17 17:46 | 85.28 | 36939.7454 | 85.84
2001-02-17 17:47 | 85.28 | 36939.7461 | 85.3933
2001-02-17 17:48 | 84.95 | 36939.7467 | 85.73
2001-02-17 17:49 | 85.62 | 36939.7474 | 86.5133
2001-02-17 17:50 | 86.29 | 36939.7481 | 86.96
2001-02-17 17:51 | 86.62 | 36939.7488 | 86.8467
2001-02-17 17:52 | 86.62 | 36939.7495 | 86.3967
2001-02-17 17:53 | 85.95 | 36939.7502 | 86.2867
2001-02-17 17:54 | 84.95 | 36939.7509 | 86.0633
2001-02-17 17:55 | 85.28 | 36939.7516 | 86.0633
2001-02-17 17:56 | 86.96 | 36939.7523 | 86.0633
2001-02-17 17:57 | 87.3 | 36939.753 | 86.1767
2001-02-17 17:58 | 86.62 | 36939.7537 | 86.29
2001-02-17 17:59 | 86.62 | 36939.7544 | 85.8433
2001-02-17 18:00 | 85.95 | 36939.7551 | 85.2867
2001-02-17 18:01 | 86.29 | 36939.7558 | 84.95
2001-02-17 18:02 | 85.95 | 36939.7565 | 85.06
2001-02-17 18:03 | 85.95 | 36939.7572 | 85.6167
2001-02-17 18:04 | 86.29 | 36939.7579 | 86.0633
2001-02-17 18:05 | 86.29 | 36939.7586 | 86.6233
2001-02-17 18:06 | 86.29 | 36939.7592 | 86.8467
2001-02-17 18:07 | 84.95 | 36939.7599 | 86.5133
2001-02-17 18:08 | 84.62 | 36939.7606 | 86.0667
2001-02-17 18:09 | 85.28 | 36939.7613 | 85.8433
2001-02-17 18:10 | 85.28 | 36939.762 | 86.1767
2001-02-17 18:11 | 86.29 | 36939.7627 | 86.4
2001-02-17 18:12 | 86.62 | 36939.7634 | 86.4
2001-02-17 18:13 | 86.96 | 36939.7641 | 86.4
2001-02-17 18:14 | 86.96 | 36939.7648 | 86.6233
2001-02-17 18:15 | 85.62 | 36939.7655 | 86.6233
2001-02-17 18:16 | 85.62 | 36939.7662 | 86.29
2001-02-17 18:17 | 86.29 | 36939.7669 | 85.8433
2001-02-17 18:18 | 86.62 | 36939.7676 | 85.62
2001-02-17 18:19 | 86.29 | 36939.7683 | 85.62
2001-02-17 18:20 | 86.29 | 36939.769 | 85.73
2001-02-17 18:21 | 86.62 | 36939.7697 | 86.0633
2001-02-17 18:22 | 86.96 | 36939.7704 | 86.3967
2001-02-17 18:23 | 86.29 | 36939.7711 | 86.62
2001-02-17 18:24 | 85.62 | 36939.7717 | 86.62
2001-02-17 18:25 | 85.62 | 36939.7724 | 86.62
2001-02-17 18:26 | 85.62 | 36939.7731 | 86.8467
2001-02-17 18:27 | 85.62 | 36939.7738 | 87.3033
2001-02-17 18:28 | 85.95 | 36939.7745 | 87.6433
2001-02-17 18:29 | 86.62 | 36939.7752 | 87.7567
2001-02-17 18:30 | 86.62 | 36939.7759 | 87.64
2001-02-17 18:31 | 86.62 | 36939.7766 | 87.5267
2001-02-17 18:32 | 86.62 | 36939.7773 | 87.5267
2001-02-17 18:33 | 86.62 | 36939.778 | 87.6433
2001-02-17 18:34 | 87.3 | 36939.7787 | 88.1033
2001-02-17 18:35 | 87.99 | 36939.7794 | 88.3333
2001-02-17 18:36 | 87.64 | 36939.7801 | 88.3333
2001-02-17 18:37 | 87.64 | 36939.7808 | 88.1033
2001-02-17 18:38 | 87.64 | 36939.7815 | 87.99
2001-02-17 18:39 | 87.3 | 36939.7822 | 87.76
2001-02-17 18:40 | 87.64 | 36939.7829 | 87.53
2001-02-17 18:41 | 87.99 | 36939.7836 | 86.9633
2001-02-17 18:42 | 88.68 | 36939.7842 | 86.85
2001-02-17 18:43 | 88.33 | 36939.7849 | 86.9633
2001-02-17 18:44 | 87.99 | 36939.7856 | 87.53
2001-02-17 18:45 | 87.99 | 36939.7863 | 87.6433
2001-02-17 18:46 | 87.99 | 36939.787 | 87.6433
2001-02-17 18:47 | 87.3 | 36939.7877 | 88.57
2001-02-17 18:48 | 87.3 | 36939.7884 | 90.1967
2001-02-17 18:49 | 86.29 | 36939.7891 | 91.59
2001-02-17 18:50 | 86.96 | 36939.7898 | 91.8233
2001-02-17 18:51 | 87.64 | 36939.7905 | 91.47
2001-02-17 18:52 | 87.99 | 36939.7912 | 91.3533
2001-02-17 18:53 | 87.3 | 36939.7919 | 91.3533
2001-02-17 18:54 | 87.64 | 36939.7926 | 91.12
2001-02-17 18:55 | 90.77 | 36939.7933 | 90.6533
2001-02-17 18:56 | 92.18 | 36939.794 | 89.9533
2001-02-17 18:57 | 91.82 | 36939.7947 | 89.49
2001-02-17 18:58 | 91.47 | 36939.7954 | 88.68
2001-02-17 18:59 | 91.12 | 36939.7961 | 88.22
2001-02-17 19:00 | 91.47 | 36939.7967 | 87.7567
2001-02-17 19:01 | 91.47 | 36939.7974 | 87.7567
2001-02-17 19:02 | 90.42 | 36939.7981 | 87.5267
2001-02-17 19:03 | 90.07 | 36939.7988 | 87.3
2001-02-17 19:04 | 89.37 | 36939.7995 | 87.0733
2001-02-17 19:05 | 89.03 | 36939.8002 | 86.7367
2001-02-17 19:06 | 87.64 | 36939.8009 | 86.1767
2001-02-17 19:07 | 87.99 | 36939.8016 | 85.84
2001-02-17 19:08 | 87.64 | 36939.8023 | 85.7267
2001-02-17 19:09 | 87.64 | 36939.803 | 86.2867
2001-02-17 19:10 | 87.3 | 36939.8037 | 86.6233
2001-02-17 19:11 | 86.96 | 36939.8044 | 87.0733
2001-02-17 19:12 | 86.96 | 36939.8051 | 87.53
2001-02-17 19:13 | 86.29 | 36939.8058 | 88.1033
2001-02-17 19:14 | 85.28 | 36939.8065 | 88.2167
2001-02-17 19:15 | 85.95 | 36939.8072 | 87.9867
2001-02-17 19:16 | 85.95 | 36939.8079 | 87.64
2001-02-17 19:17 | 86.96 | 36939.8086 | 87.7567
2001-02-17 19:18 | 86.96 | 36939.8092 | 87.8733
2001-02-17 19:19 | 87.3 | 36939.8099 | 88.1033
2001-02-17 19:20 | 88.33 | 36939.8106 | 88.2167
2001-02-17 19:21 | 88.68 | 36939.8113 | 88.2167
2001-02-17 19:22 | 87.64 | 36939.812 | 87.9867
2001-02-17 19:23 | 87.64 | 36939.8127 | 87.3067
2001-02-17 19:24 | 87.64 | 36939.8134 | 86.5167
2001-02-17 19:25 | 87.99 | 36939.8141 | 85.73
2001-02-17 19:26 | 87.99 | 36939.8148 | 85.2833
2001-02-17 19:27 | 88.33 | 36939.8155 | 85.17
2001-02-17 19:28 | 88.33 | 36939.8162 | 85.2833
2001-02-17 19:29 | 87.99 | 36939.8169 | 85.5067
2001-02-17 19:30 | 87.64 | 36939.8176 | 85.62
2001-02-17 19:31 | 86.29 | 36939.8183 | 85.62
2001-02-17 19:32 | 85.62 | 36939.819 | 85.62
2001-02-17 19:33 | 85.28 | 36939.8197 | 85.8433
2001-02-17 19:34 | 84.95 | 36939.8204 | 86.0667
2001-02-17 19:35 | 85.28 | 36939.8211 | 86.29
2001-02-17 19:36 | 85.62 | 36939.8217 | 86.1767
2001-02-17 19:37 | 85.62 | 36939.8224 | 85.73
2001-02-17 19:38 | 85.62 | 36939.8231 | 85.3933
2001-02-17 19:39 | 85.62 | 36939.8238 | 85.3933
2001-02-17 19:40 | 85.62 | 36939.8245 | 85.84
2001-02-17 19:41 | 86.29 | 36939.8252 | 86.2867
2001-02-17 19:42 | 86.29 | 36939.8259 | 86.51
2001-02-17 19:43 | 86.29 | 36939.8266 | 86.3967
2001-02-17 19:44 | 85.95 | 36939.8273 | 85.95
2001-02-17 19:45 | 84.95 | 36939.828 | 85.5033
2001-02-17 19:46 | 85.28 | 36939.8287 | 85.06
2001-02-17 19:47 | 85.95 | 36939.8294 | 84.95
2001-02-17 19:48 | 86.29 | 36939.8301 | 84.73
2001-02-17 19:49 | 86.62 | 36939.8308 | 84.84
2001-02-17 19:50 | 86.62 | 36939.8315 | 84.95
2001-02-17 19:51 | 85.95 | 36939.8322 | 85.73
2001-02-17 19:52 | 85.28 | 36939.8329 | 86.5133
2001-02-17 19:53 | 85.28 | 36939.8336 | 87.3
2001-02-17 19:54 | 84.62 | 36939.8342 | 87.5267
2001-02-17 19:55 | 84.95 | 36939.8349 | 87.7567
2001-02-17 19:56 | 84.62 | 36939.8356 | 88.8
2001-02-17 19:57 | 84.95 | 36939.8363 | 90.5533
2001-02-17 19:58 | 85.28 | 36939.837 | 92.6767
2001-02-17 19:59 | 86.96 | 36939.8377 | 93.63
2001-02-17 20:00 | 87.3 | 36939.8384 | 93.63
2001-02-17 20:01 | 87.64 | 36939.8391 | 93.0233
2001-02-17 20:02 | 87.64 | 36939.8398 | 92.54
2001-02-17 20:03 | 87.99 | 36939.8405 | 92.0633
2001-02-17 20:04 | 90.77 | 36939.8412 | 91.59
2001-02-17 20:05 | 92.9 | 36939.8419 | 91.12
2001-02-17 20:06 | 94.36 | 36939.8426 | 90.8867
2001-02-17 20:07 | 93.63 | 36939.8433 | 90.6533
2001-02-17 20:08 | 92.9 | 36939.844 | 90.42
2001-02-17 20:09 | 92.54 | 36939.8447 | 90.1867
2001-02-17 20:10 | 92.18 | 36939.8454 | 90.07
2001-02-17 20:11 | 91.47 | 36939.8461 | 89.0333
2001-02-17 20:12 | 91.12 | 36939.8467 | 87.4367
2001-02-17 20:13 | 90.77 | 36939.8474 | 85.9533
2001-02-17 20:14 | 90.77 | 36939.8481 | 85.5067
2001-02-17 20:15 | 90.42 | 36939.8488 | 85.8433
2001-02-17 20:16 | 90.07 | 36939.8495 | 86.0667
2001-02-17 20:17 | 90.07 | 36939.8502 | 86.4
2001-02-17 20:18 | 90.07 | 36939.8509 | 86.85
2001-02-17 20:19 | 86.96 | 36939.8516 | 87.3
2001-02-17 20:20 | 85.28 | 36939.8523 | 87.3
2001-02-17 20:21 | 85.62 | 36939.853 | 86.5133
2001-02-17 20:22 | 85.62 | 36939.8537 | 85.6167
2001-02-17 20:23 | 86.29 | 36939.8544 | 84.95
2001-02-17 20:24 | 86.29 | 36939.8551 | 84.84
2001-02-17 20:25 | 86.62 | 36939.8558 | 85.0633
2001-02-17 20:26 | 87.64 | 36939.8565 | 85.1733
2001-02-17 20:27 | 87.64 | 36939.8572 | 85.1733
2001-02-17 20:28 | 86.62 | 36939.8579 | 84.95
2001-02-17 20:29 | 85.28 | 36939.8586 | 84.95
2001-02-17 20:30 | 84.95 | 36939.8592 | 85.06
2001-02-17 20:31 | 84.62 | 36939.8599 | 85.17
2001-02-17 20:32 | 84.95 | 36939.8606 | 85.3933
2001-02-17 20:33 | 85.62 | 36939.8613 | 85.5067
2001-02-17 20:34 | 84.95 | 36939.862 | 85.62
2001-02-17 20:35 | 84.95 | 36939.8627 | 85.62
2001-02-17 20:36 | 84.95 | 36939.8634 | 85.62
2001-02-17 20:37 | 84.95 | 36939.8641 | 85.5067
2001-02-17 20:38 | 85.28 | 36939.8648 | 85.2833
2001-02-17 20:39 | 85.28 | 36939.8655 | 85.06
2001-02-17 20:40 | 85.62 | 36939.8662 | 85.06
2001-02-17 20:41 | 85.62 | 36939.8669 | 85.17
2001-02-17 20:42 | 85.62 | 36939.8676 | 85.28
2001-02-17 20:43 | 85.62 | 36939.8683 | 85.17
2001-02-17 20:44 | 85.62 | 36939.869 | 85.5067
2001-02-17 20:45 | 85.28 | 36939.8697 | 86.0667
2001-02-17 20:46 | 84.95 | 36939.8704 | 86.85
2001-02-17 20:47 | 84.95 | 36939.8711 | 87.1867
2001-02-17 20:48 | 85.28 | 36939.8717 | 87.1867
2001-02-17 20:49 | 85.28 | 36939.8724 | 88.2267
2001-02-17 20:50 | 85.28 | 36939.8731 | 90.0933
2001-02-17 20:51 | 84.95 | 36939.8738 | 92.4367
2001-02-17 20:52 | 86.29 | 36939.8745 | 93.6267
2001-02-17 20:53 | 86.96 | 36939.8752 | 93.6267
2001-02-17 20:54 | 87.3 | 36939.8759 | 93.2633
2001-02-17 20:55 | 87.3 | 36939.8766 | 92.66
2001-02-17 20:56 | 86.96 | 36939.8773 | 92.3
2001-02-17 20:57 | 90.42 | 36939.878 | 92.06
2001-02-17 20:58 | 92.9 | 36939.8787 | 92.18
2001-02-17 20:59 | 93.99 | 36939.8794 | 92.18
2001-02-17 21:00 | 93.99 | 36939.8801 | 91.9433
2001-02-17 21:01 | 92.9 | 36939.8808 | 91.2367
2001-02-17 21:02 | 92.9 | 36939.8815 | 90.77
2001-02-17 21:03 | 92.18 | 36939.8822 | 90.42
2001-02-17 21:04 | 91.82 | 36939.8829 | 89.61
2001-02-17 21:05 | 92.18 | 36939.8836 | 88.3433
2001-02-17 21:06 | 92.54 | 36939.8842 | 86.8533
2001-02-17 21:07 | 91.82 | 36939.8849 | 86.1733
2001-02-17 21:08 | 91.47 | 36939.8856 | 86.0633
2001-02-17 21:09 | 90.42 | 36939.8863 | 86.0633
2001-02-17 21:10 | 90.42 | 36939.887 | 86.0633
2001-02-17 21:11 | 90.42 | 36939.8877 | 85.95
2001-02-17 21:12 | 87.99 | 36939.8884 | 85.7267
2001-02-17 21:13 | 86.62 | 36939.8891 | 85.5033
2001-02-17 21:14 | 85.95 | 36939.8898 | 85.06
2001-02-17 21:15 | 85.95 | 36939.8905 | 84.84
2001-02-17 21:16 | 86.29 | 36939.8912 | 84.73
2001-02-17 21:17 | 85.95 | 36939.8919 | 84.62
2001-02-17 21:18 | 85.95 | 36939.8926 | 84.51
2001-02-17 21:19 | 85.95 | 36939.8933 | 84.4
2001-02-17 21:20 | 85.28 | 36939.894 | 84.51
2001-02-17 21:21 | 85.28 | 36939.8947 | 84.73
2001-02-17 21:22 | 84.62 | 36939.8954 | 84.95
2001-02-17 21:23 | 84.62 | 36939.8961 | 85.17
2001-02-17 21:24 | 84.95 | 36939.8967 | 85.3933
2001-02-17 21:25 | 84.29 | 36939.8974 | 85.6167
2001-02-17 21:26 | 84.29 | 36939.8981 | 85.84
2001-02-17 21:27 | 84.62 | 36939.8988 | 86.0633
2001-02-17 21:28 | 84.62 | 36939.8995 | 86.2867
2001-02-17 21:29 | 84.95 | 36939.9002 | 86.7367
2001-02-17 21:30 | 85.28 | 36939.9009 | 87.5333
2001-02-17 21:31 | 85.28 | 36939.9016 | 88.1033
2001-02-17 21:32 | 85.62 | 36939.9023 | 88.4467
2001-02-17 21:33 | 85.95 | 36939.903 | 88.4467
2001-02-17 21:34 | 85.95 | 36939.9037 | 89.0267
2001-02-17 21:35 | 86.29 | 36939.9044 | 90.9133
2001-02-17 21:36 | 86.62 | 36939.9051 | 93.4233
2001-02-17 21:37 | 87.3 | 36939.9058 | 95.5967
2001-02-17 21:38 | 88.68 | 36939.9065 | 96.3367
2001-02-17 21:39 | 88.33 | 36939.9072 | 96.2133
2001-02-17 21:40 | 88.33 | 36939.9079 | 95.7167
2001-02-17 21:41 | 88.68 | 36939.9086 | 95.5933
2001-02-17 21:42 | 90.07 | 36939.9092 | 95.5933
2001-02-17 21:43 | 93.99 | 36939.9099 | 95.5933
2001-02-17 21:44 | 96.21 | 36939.9106 | 95.2233
2001-02-17 21:45 | 96.59 | 36939.9113 | 94.73
2001-02-17 21:46 | 96.21 | 36939.912 | 94.4833
2001-02-17 21:47 | 95.84 | 36939.9127 | 93.9933
2001-02-17 21:48 | 95.1 | 36939.9134 | 93.3867
2001-02-17 21:49 | 95.84 | 36939.9141 | 92.0733
2001-02-17 21:50 | 95.84 | 36939.9148 | 90.6633
2001-02-17 21:51 | 95.1 | 36939.9155 | 89.03
2001-02-17 21:52 | 94.73 | 36939.9162 | 87.99
2001-02-17 21:53 | 94.36 | 36939.9169 | 87.1867
2001-02-17 21:54 | 94.36 | 36939.9176 | 86.29
2001-02-17 21:55 | 93.26 | 36939.9183 | 85.3967
2001-02-17 21:56 | 92.54 | 36939.919 | 84.62
2001-02-17 21:57 | 90.42 | 36939.9197 | 84.51
2001-02-17 21:58 | 89.03 | 36939.9204 | 84.62
2001-02-17 21:59 | 87.64 | 36939.9211 | 84.95
2001-02-17 22:00 | 87.3 | 36939.9217 | 85.2833
2001-02-17 22:01 | 86.62 | 36939.9224 | 85.5067
2001-02-17 22:02 | 84.95 | 36939.9231 | 85.73
2001-02-17 22:03 | 84.62 | 36939.9238 | 85.84
2001-02-17 22:04 | 84.29 | 36939.9245 | 85.95
2001-02-17 22:05 | 84.62 | 36939.9252 | 86.0633
2001-02-17 22:06 | 84.95 | 36939.9259 | 86.1767
2001-02-17 22:07 | 85.28 | 36939.9266 | 86.29
2001-02-17 22:08 | 85.62 | 36939.9273 | 86.1767
2001-02-17 22:09 | 85.62 | 36939.928 | 86.0633
2001-02-17 22:10 | 85.95 | 36939.9287 | 86.0633
2001-02-17 22:11 | 85.95 | 36939.9294 | 86.2867
2001-02-17 22:12 | 85.95 | 36939.9301 | 86.6233
2001-02-17 22:13 | 86.29 | 36939.9308 | 87.0733
2001-02-17 22:14 | 86.29 | 36939.9315 | 87.4133
2001-02-17 22:15 | 86.29 | 36939.9322 | 87.7567
2001-02-17 22:16 | 85.95 | 36939.9329 | 87.8733
2001-02-17 22:17 | 85.95 | 36939.9336 | 88.5667
2001-02-17 22:18 | 86.29 | 36939.9342 | 89.3767
2001-02-17 22:19 | 86.62 | 36939.9349 | 91.2567
2001-02-17 22:20 | 86.96 | 36939.9356 | 92.8033
2001-02-17 22:21 | 87.64 | 36939.9363 | 94.3633
2001-02-17 22:22 | 87.64 | 36939.937 | 95.98
2001-02-17 22:23 | 87.99 | 36939.9377 | 97.48
2001-02-17 22:24 | 87.99 | 36939.9384 | 98.99
2001-02-17 22:25 | 89.72 | 36939.9391 | 99.2467
2001-02-17 22:26 | 90.42 | 36939.9398 | 99.12
2001-02-17 22:27 | 93.63 | 36939.9405 | 98.7367
2001-02-17 22:28 | 94.36 | 36939.9412 | 98.48
2001-02-17 22:29 | 95.1 | 36939.9419 | 98.48
2001-02-17 22:30 | 98.48 | 36939.9426 | 98.48
2001-02-17 22:31 | 98.86 | 36939.9433 | 98.2267
2001-02-17 22:32 | 99.63 | 36939.944 | 97.72
2001-02-17 22:33 | 99.25 | 36939.9447 | 96.5933
2001-02-17 22:34 | 98.48 | 36939.9454 | 95.23
2001-02-17 22:35 | 98.48 | 36939.9461 | 93.7567
2001-02-17 22:36 | 98.48 | 36939.9467 | 93.1433
2001-02-17 22:37 | 98.48 | 36939.9474 | 93.1433
2001-02-17 22:38 | 98.48 | 36939.9481 | 93.6267
2001-02-17 22:39 | 97.72 | 36939.9488 | 93.87
2001-02-17 22:40 | 96.96 | 36939.9495 | 94.1133
2001-02-17 22:41 | 95.1 | 36939.9502 | 94.36
2001-02-17 22:42 | 93.63 | 36939.9509 | 94.73
2001-02-17 22:43 | 92.54 | 36939.9516 | 94.9767
2001-02-17 22:44 | 93.26 | 36939.9523 | 95.1
2001-02-17 22:45 | 93.63 | 36939.953 | 94.9767
2001-02-17 22:46 | 93.99 | 36939.9537 | 94.9767
2001-02-17 22:47 | 93.99 | 36939.9544 | 94.9767
2001-02-17 22:48 | 94.36 | 36939.9551 | 95.1
2001-02-17 22:49 | 94.73 | 36939.9558 | 94.9767
2001-02-17 22:50 | 95.1 | 36939.9565 | 94.4867
2001-02-17 22:51 | 95.1 | 36939.9572 | 93.8733
2001-02-17 22:52 | 95.1 | 36939.9579 | 93.2633
2001-02-17 22:53 | 94.73 | 36939.9586 | 92.9
2001-02-17 22:54 | 95.1 | 36939.9592 | 92.78
2001-02-17 22:55 | 95.1 | 36939.9599 | 92.78
2001-02-17 22:56 | 95.1 | 36939.9606 | 92.9
2001-02-17 22:57 | 94.73 | 36939.9613 | 92.78
2001-02-17 22:58 | 93.63 | 36939.962 | 92.66
2001-02-17 22:59 | 93.26 | 36939.9627 | 92.54
2001-02-17 23:00 | 92.9 | 36939.9634 | 92.54
2001-02-17 23:01 | 92.54 | 36939.9641 | 92.54
2001-02-17 23:02 | 92.9 | 36939.9648 | 92.54
2001-02-17 23:03 | 92.9 | 36939.9655 | 92.42
2001-02-17 23:04 | 92.9 | 36939.9662 | 92.3
2001-02-17 23:05 | 92.54 | 36939.9669 | 92.06
2001-02-17 23:06 | 92.54 | 36939.9676 | 91.94
2001-02-17 23:07 | 92.54 | 36939.9683 | 91.82
2001-02-17 23:08 | 92.54 | 36939.969 | 91.94
2001-02-17 23:09 | 92.54 | 36939.9697 | 92.06
2001-02-17 23:10 | 92.54 | 36939.9704 | 92.06
2001-02-17 23:11 | 92.18 | 36939.9711 | 91.94
2001-02-17 23:12 | 92.18 | 36939.9717 | 91.82
2001-02-17 23:13 | 91.82 | 36939.9724 | 91.82
2001-02-17 23:14 | 91.82 | 36939.9731 | 91.82
2001-02-17 23:15 | 91.82 | 36939.9738 | 91.82
2001-02-17 23:16 | 92.18 | 36939.9745 | 91.7033
2001-02-17 23:17 | 92.18 | 36939.9752 | 91.7033
2001-02-17 23:18 | 91.82 | 36939.9759 | 91.7033
2001-02-17 23:19 | 91.82 | 36939.9766 | 92.06
2001-02-17 23:20 | 91.82 | 36939.9773 | 92.7833
2001-02-17 23:21 | 91.82 | 36939.978 | 93.63
2001-02-17 23:22 | 91.82 | 36939.9787 | 94.2367
2001-02-17 23:23 | 91.82 | 36939.9794 | 94.4833
2001-02-17 23:24 | 91.47 | 36939.9801 | 95.2267
2001-02-17 23:25 | 91.82 | 36939.9808 | 96.3467
2001-02-17 23:26 | 91.82 | 36939.9815 | 97.47
2001-02-17 23:27 | 92.54 | 36939.9822 | 98.2267
2001-02-17 23:28 | 93.99 | 36939.9829 | 98.2267
2001-02-17 23:29 | 94.36 | 36939.9836 | 97.8467
2001-02-17 23:30 | 94.36 | 36939.9842 | 97.2133
2001-02-17 23:31 | 94.73 | 36939.9849 | 96.8367
2001-02-17 23:32 | 96.59 | 36939.9856 | 96.4633
2001-02-17 23:33 | 97.72 | 36939.9863 | 95.8433
2001-02-17 23:34 | 98.1 | 36939.987 | 94.8567
2001-02-17 23:35 | 98.86 | 36939.9877 | 93.6367
2001-02-17 23:36 | 97.72 | 36939.9884 | 91.4967
2001-02-17 23:37 | 96.96 | 36939.9891 | 89.8467
2001-02-17 23:38 | 96.96 | 36939.9898 | 88.5633
2001-02-17 23:39 | 96.59 | 36939.9905 | 88.3333
2001-02-17 23:40 | 95.84 | 36939.9912 | 87.4233
2001-02-17 23:41 | 95.1 | 36939.9919 | 86.1867
2001-02-17 23:42 | 93.63 | 36939.9926 | 84.8433
2001-02-17 23:43 | 92.18 | 36939.9933 | 84.07
2001-02-17 23:44 | 88.68 | 36939.994 | 83.85
2001-02-17 23:45 | 88.68 | 36939.9947 | 83.96
2001-02-17 23:46 | 88.33 | 36939.9954 | 84.18
2001-02-17 23:47 | 87.99 | 36939.9961 | 84.29
2001-02-17 23:48 | 85.95 | 36939.9967 | 84.29
2001-02-17 23:49 | 84.62 | 36939.9974 | 84.29
2001-02-17 23:50 | 83.96 | 36939.9981 | 84.29
2001-02-17 23:51 | 83.63 | 36939.9988 | 84.29
2001-02-17 23:52 | 83.96 | 36939.9995 | 84.51
2001-02-17 23:53 | 84.29 | 36940.0002 | 84.73
2001-02-17 23:54 | 84.29 | 36940.0009 | 84.73
2001-02-17 23:55 | 84.29 | 36940.0016 | 84.51
2001-02-17 23:56 | 84.29 | 36940.0023 | 84.29
2001-02-17 23:57 | 84.29 | 36940.003 | 84.29
2001-02-17 23:58 | 84.29 | 36940.0037 | 84.29
2001-02-17 23:59 | 84.29 | 36940.0044 | 85.7533
2001-02-18 | 84.95 | 36940.0051 | 88.1467
2001-02-18 00:01 | 84.95 | 36940.0058 | 90.6567
2001-02-18 00:02 | 84.29 | 36940.0065 | 91.7033
2001-02-18 00:03 | 84.29 | 36940.0072 | 91.94
2001-02-18 00:04 | 84.29 | 36940.0079 | 91.94
2001-02-18 00:05 | 84.29 | 36940.0086 | 93.6533
2001-02-18 00:06 | 84.29 | 36940.0092 | 96.2667
2001-02-18 00:07 | 88.68 | 36940.0099 | 99
2001-02-18 00:08 | 91.47 | 36940.0106 | 100.02
2001-02-18 00:09 | 91.82 | 36940.0113 | 100.02
2001-02-18 00:10 | 91.82 | 36940.012 | 100.02
2001-02-18 00:11 | 92.18 | 36940.0127 | 100.02
2001-02-18 00:12 | 91.82 | 36940.0134 | 100.02
2001-02-18 00:13 | 96.96 | 36940.0141 | 99.89
2001-02-18 00:14 | 100.02 | 36940.0148 | 99.76
2001-02-18 00:15 | 100.02 | 36940.0155 | 99.63
2001-02-18 00:16 | 100.02 | 36940.0162 | 99.5033
2001-02-18 00:17 | 100.02 | 36940.0169 | 99.2467
2001-02-18 00:18 | 100.02 | 36940.0176 | 98.99
2001-02-18 00:19 | 100.02 | 36940.0183 | 98.2267
2001-02-18 00:20 | 100.02 | 36940.019 | 98.2267
2001-02-18 00:21 | 99.63 | 36940.0197 | 98.6133
2001-02-18 00:22 | 99.63 | 36940.0204 | 99.6333
2001-02-18 00:23 | 99.63 | 36940.0211 | 100.02
2001-02-18 00:24 | 99.25 | 36940.0217 | 100.02
2001-02-18 00:25 | 98.86 | 36940.0224 | 100.02
2001-02-18 00:26 | 98.86 | 36940.0231 | 100.02
2001-02-18 00:27 | 96.96 | 36940.0238 | 100.02
2001-02-18 00:28 | 98.86 | 36940.0245 | 100.02
2001-02-18 00:29 | 100.02 | 36940.0252 | 100.02
2001-02-18 00:30 | 100.02 | 36940.0259 | 100.02
2001-02-18 00:31 | 100.02 | 36940.0266 | 100.02
2001-02-18 00:32 | 100.02 | 36940.0273 | 100.02
2001-02-18 00:33 | 100.02 | 36940.028 | 100.02
2001-02-18 00:34 | 100.02 | 36940.0287 | 99.89
2001-02-18 00:35 | 100.02 | 36940.0294 | 99.6333
2001-02-18 00:36 | 100.02 | 36940.0301 | 99.12
2001-02-18 00:37 | 100.02 | 36940.0308 | 98.61
2001-02-18 00:38 | 100.02 | 36940.0315 | 97.35
2001-02-18 00:39 | 100.02 | 36940.0322 | 96.2233
2001-02-18 00:40 | 100.02 | 36940.0329 | 95.47
2001-02-18 00:41 | 100.02 | 36940.0336 | 94.02
2001-02-18 00:42 | 99.63 | 36940.0342 | 92.3433
2001-02-18 00:43 | 99.25 | 36940.0349 | 90.1867
2001-02-18 00:44 | 98.48 | 36940.0356 | 89.72
2001-02-18 00:45 | 98.1 | 36940.0363 | 89.8367
2001-02-18 00:46 | 95.47 | 36940.037 | 89.49
2001-02-18 00:47 | 95.1 | 36940.0377 | 89.49
2001-02-18 00:48 | 95.84 | 36940.0384 | 89.2567
2001-02-18 00:49 | 91.12 | 36940.0391 | 89.2567
2001-02-18 00:50 | 90.07 | 36940.0398 | 89.14
2001-02-18 00:51 | 89.37 | 36940.0405 | 88.91
2001-02-18 00:52 | 89.72 | 36940.0412 | 88.91
2001-02-18 00:53 | 90.42 | 36940.0419 | 88.3333
2001-02-18 00:54 | 88.33 | 36940.0426 | 87.9867
2001-02-18 00:55 | 89.72 | 36940.0433 | 88.22
2001-02-18 00:56 | 89.72 | 36940.044 | 88.3367
2001-02-18 00:57 | 88.33 | 36940.0447 | 88.45
2001-02-18 00:58 | 89.37 | 36940.0454 | 88.45
2001-02-18 00:59 | 89.03 | 36940.0461 | 88.7967
2001-02-18 01:00 | 88.33 | 36940.0467 | 89.03
2001-02-18 01:01 | 87.64 | 36940.0474 | 88.4533
2001-02-18 01:02 | 87.99 | 36940.0481 | 88.22
2001-02-18 01:03 | 89.03 | 36940.0488 | 87.9867
2001-02-18 01:04 | 87.99 | 36940.0495 | 88.1
2001-02-18 01:05 | 88.33 | 36940.0502 | 87.87
2001-02-18 01:06 | 89.03 | 36940.0509 | 87.7567
2001-02-18 01:07 | 89.03 | 36940.0516 | 87.7567
2001-02-18 01:08 | 89.03 | 36940.0523 | 87.8733
2001-02-18 01:09 | 87.3 | 36940.053 | 87.8733
2001-02-18 01:10 | 88.33 | 36940.0537 | 87.99
2001-02-18 01:11 | 88.33 | 36940.0544 | 87.8733
2001-02-18 01:12 | 87.64 | 36940.0551 | 87.8733
2001-02-18 01:13 | 87.64 | 36940.0558 | 87.8733
2001-02-18 01:14 | 87.99 | 36940.0565 | 87.76
2001-02-18 01:15 | 87.64 | 36940.0572 | 87.53
2001-02-18 01:16 | 87.99 | 36940.0579 | 87.3
2001-02-18 01:17 | 87.99 | 36940.0586 | 87.3
2001-02-18 01:18 | 87.99 | 36940.0592 | 87.4133
2001-02-18 01:19 | 87.64 | 36940.0599 | 87.7567
2001-02-18 01:20 | 87.99 | 36940.0606 | 87.87
2001-02-18 01:21 | 87.99 | 36940.0613 | 87.9867
2001-02-18 01:22 | 87.3 | 36940.062 | 87.9867
2001-02-18 01:23 | 87.3 | 36940.0627 | 88.2167
2001-02-18 01:24 | 87.3 | 36940.0634 | 88.33
2001-02-18 01:25 | 87.3 | 36940.0641 | 88.33
2001-02-18 01:26 | 87.64 | 36940.0648 | 88.33
2001-02-18 01:27 | 88.33 | 36940.0655 | 87.76
2001-02-18 01:28 | 87.64 | 36940.0662 | 87.3033
2001-02-18 01:29 | 87.99 | 36940.0669 | 86.96
2001-02-18 01:30 | 88.33 | 36940.0676 | 87.1867
2001-02-18 01:31 | 88.33 | 36940.0683 | 87.4133
2001-02-18 01:32 | 88.33 | 36940.069 | 87.5267
2001-02-18 01:33 | 88.33 | 36940.0697 | 87.64
2001-02-18 01:34 | 88.33 | 36940.0704 | 87.64
2001-02-18 01:35 | 86.62 | 36940.0711 | 87.64
2001-02-18 01:36 | 86.96 | 36940.0717 | 87.7567
2001-02-18 01:37 | 87.3 | 36940.0724 | 87.8733
2001-02-18 01:38 | 87.3 | 36940.0731 | 87.99
2001-02-18 01:39 | 87.64 | 36940.0738 | 87.76
2001-02-18 01:40 | 87.64 | 36940.0745 | 87.53
2001-02-18 01:41 | 87.64 | 36940.0752 | 87.1867
2001-02-18 01:42 | 87.64 | 36940.0759 | 87.1867
2001-02-18 01:43 | 87.64 | 36940.0766 | 87.0733
2001-02-18 01:44 | 87.99 | 36940.0773 | 87.0733
2001-02-18 01:45 | 87.99 | 36940.078 | 86.8467
2001-02-18 01:46 | 87.99 | 36940.0787 | 86.6233
2001-02-18 01:47 | 87.3 | 36940.0794 | 86.51
2001-02-18 01:48 | 87.3 | 36940.0801 | 86.51
2001-02-18 01:49 | 86.96 | 36940.0808 | 86.62
2001-02-18 01:50 | 87.3 | 36940.0815 | 86.62
2001-02-18 01:51 | 86.96 | 36940.0822 | 86.62
2001-02-18 01:52 | 86.96 | 36940.0829 | 86.62
2001-02-18 01:53 | 86.62 | 36940.0836 | 86.62
2001-02-18 01:54 | 86.29 | 36940.0842 | 86.62
2001-02-18 01:55 | 86.62 | 36940.0849 | 86.62
2001-02-18 01:56 | 86.62 | 36940.0856 | 86.62
2001-02-18 01:57 | 86.62 | 36940.0863 | 86.62
2001-02-18 01:58 | 86.62 | 36940.087 | 86.62
2001-02-18 01:59 | 86.62 | 36940.0877 | 86.62
2001-02-18 02:00 | 86.62 | 36940.0884 | 86.62
2001-02-18 02:01 | 86.62 | 36940.0891 | 86.62
2001-02-18 02:02 | 86.62 | 36940.0898 | 86.62
2001-02-18 02:03 | 86.62 | 36940.0905 | 86.62
2001-02-18 02:04 | 86.62 | 36940.0912 | 86.62
2001-02-18 02:05 | 86.62 | 36940.0919 | 86.62
2001-02-18 02:06 | 86.62 | 36940.0926 | 86.62
2001-02-18 02:07 | 86.62 | 36940.0933 | 86.62
2001-02-18 02:08 | 86.62 | 36940.094 | 86.62
2001-02-18 02:09 | 86.62 | 36940.0947 | 86.62
2001-02-18 02:10 | 86.62 | 36940.0954 | 86.51
2001-02-18 02:11 | 86.62 | 36940.0961 | 86.4
2001-02-18 02:12 | 86.62 | 36940.0967 | 86.29
2001-02-18 02:13 | 86.62 | 36940.0974 | 86.29
2001-02-18 02:14 | 86.62 | 36940.0981 | 86.29
2001-02-18 02:15 | 86.62 | 36940.0988 | 86.29
2001-02-18 02:16 | 86.62 | 36940.0995 | 86.4
2001-02-18 02:17 | 86.62 | 36940.1002 | 86.51
2001-02-18 02:18 | 86.29 | 36940.1009 | 86.62
2001-02-18 02:19 | 86.29 | 36940.1016 | 86.62
2001-02-18 02:20 | 86.29 | 36940.1023 | 86.62
2001-02-18 02:21 | 86.29 | 36940.103 | 86.62
2001-02-18 02:22 | 86.29 | 36940.1037 | 86.51
2001-02-18 02:23 | 86.29 | 36940.1044 | 86.4
2001-02-18 02:24 | 86.62 | 36940.1051 | 86.29
2001-02-18 02:25 | 86.62 | 36940.1058 | 86.29
2001-02-18 02:26 | 86.62 | 36940.1065 | 86.29
2001-02-18 02:27 | 86.62 | 36940.1072 | 86.29
2001-02-18 02:28 | 86.62 | 36940.1079 | 86.1767
2001-02-18 02:29 | 86.62 | 36940.1086 | 86.0633
2001-02-18 02:30 | 86.29 | 36940.1092 | 85.95
2001-02-18 02:31 | 86.29 | 36940.1099 | 85.95
2001-02-18 02:32 | 86.29 | 36940.1106 | 85.95
2001-02-18 02:33 | 86.29 | 36940.1113 | 85.84
2001-02-18 02:34 | 86.29 | 36940.112 | 85.73
2001-02-18 02:35 | 86.29 | 36940.1127 | 85.62
2001-02-18 02:36 | 85.95 | 36940.1134 | 85.62
2001-02-18 02:37 | 85.95 | 36940.1141 | 85.62
2001-02-18 02:38 | 85.95 | 36940.1148 | 85.62
2001-02-18 02:39 | 85.95 | 36940.1155 | 85.62
2001-02-18 02:40 | 85.95 | 36940.1162 | 85.62
2001-02-18 02:41 | 85.62 | 36940.1169 | 85.62
2001-02-18 02:42 | 85.62 | 36940.1176 | 85.62
2001-02-18 02:43 | 85.62 | 36940.1183 | 85.62
2001-02-18 02:44 | 85.62 | 36940.119 | 85.62
2001-02-18 02:45 | 85.62 | 36940.1197 | 85.73
2001-02-18 02:46 | 85.62 | 36940.1204 | 85.84
2001-02-18 02:47 | 85.62 | 36940.1211 | 86.1733
2001-02-18 02:48 | 85.62 | 36940.1217 | 86.51
2001-02-18 02:49 | 85.62 | 36940.1224 | 86.8467
2001-02-18 02:50 | 85.62 | 36940.1231 | 87.0733
2001-02-18 02:51 | 85.62 | 36940.1238 | 87.1867
2001-02-18 02:52 | 85.62 | 36940.1245 | 87.3
2001-02-18 02:53 | 85.95 | 36940.1252 | 87.4133
2001-02-18 02:54 | 85.95 | 36940.1259 | 87.5267
2001-02-18 02:55 | 86.62 | 36940.1266 | 87.7567
2001-02-18 02:56 | 86.96 | 36940.1273 | 87.7567
2001-02-18 02:57 | 86.96 | 36940.128 | 87.8733
2001-02-18 02:58 | 87.3 | 36940.1287 | 87.7567
2001-02-18 02:59 | 87.3 | 36940.1294 | 87.6433
2001-02-18 03:00 | 87.3 | 36940.1301 | 87.3
2001-02-18 03:01 | 87.64 | 36940.1308 | 86.96
2001-02-18 03:02 | 87.64 | 36940.1315 | 86.7333
2001-02-18 03:03 | 87.99 | 36940.1322 | 86.51
2001-02-18 03:04 | 87.64 | 36940.1329 | 86.0633
2001-02-18 03:05 | 87.99 | 36940.1336 | 85.6167
2001-02-18 03:06 | 87.64 | 36940.1342 | 85.28
2001-02-18 03:07 | 87.3 | 36940.1349 | 85.3933
2001-02-18 03:08 | 86.96 | 36940.1356 | 85.5067
2001-02-18 03:09 | 86.62 | 36940.1363 | 85.62
2001-02-18 03:10 | 86.62 | 36940.137 | 85.2867
2001-02-18 03:11 | 86.29 | 36940.1377 | 84.9533
2001-02-18 03:12 | 85.28 | 36940.1384 | 84.29
2001-02-18 03:13 | 85.28 | 36940.1391 | 83.85
2001-02-18 03:14 | 85.28 | 36940.1398 | 82.9733
2001-02-18 03:15 | 85.62 | 36940.1405 | 82.1033
2001-02-18 03:16 | 85.62 | 36940.1412 | 81.2367
2001-02-18 03:17 | 85.62 | 36940.1419 | 80.7
2001-02-18 03:18 | 84.62 | 36940.1426 | 79.8567
2001-02-18 03:19 | 84.62 | 36940.1433 | 79.0167
2001-02-18 03:20 | 83.63 | 36940.144 | 78.2833
2001-02-18 03:21 | 83.3 | 36940.1447 | 78.18
2001-02-18 03:22 | 81.99 | 36940.1454 | 78.18
2001-02-18 03:23 | 81.02 | 36940.1461 | 78.2833
2001-02-18 03:24 | 80.7 | 36940.1467 | 78.4933
2001-02-18 03:25 | 80.38 | 36940.1474 | 78.8067
2001-02-18 03:26 | 78.49 | 36940.1481 | 79.1233
2001-02-18 03:27 | 78.18 | 36940.1488 | 79.3333
2001-02-18 03:28 | 78.18 | 36940.1495 | 79.44
2001-02-18 03:29 | 78.18 | 36940.1502 | 79.3333
2001-02-18 03:30 | 78.18 | 36940.1509 | 79.2267
2001-02-18 03:31 | 78.49 | 36940.1516 | 79.2267
2001-02-18 03:32 | 78.81 | 36940.1523 | 79.3333
2001-02-18 03:33 | 79.12 | 36940.153 | 79.44
2001-02-18 03:34 | 79.44 | 36940.1537 | 79.5433
2001-02-18 03:35 | 79.44 | 36940.1544 | 79.6467
2001-02-18 03:36 | 79.44 | 36940.1551 | 79.8567
2001-02-18 03:37 | 79.12 | 36940.1558 | 79.9633
2001-02-18 03:38 | 79.12 | 36940.1565 | 80.07
2001-02-18 03:39 | 79.44 | 36940.1572 | 79.9633
2001-02-18 03:40 | 79.44 | 36940.1579 | 79.9633
2001-02-18 03:41 | 79.44 | 36940.1586 | 79.7533
2001-02-18 03:42 | 79.75 | 36940.1592 | 79.5433
2001-02-18 03:43 | 79.75 | 36940.1599 | 79.2267
2001-02-18 03:44 | 80.07 | 36940.1606 | 79.0167
2001-02-18 03:45 | 80.07 | 36940.1613 | 78.9133
2001-02-18 03:46 | 80.07 | 36940.162 | 78.7033
2001-02-18 03:47 | 79.75 | 36940.1627 | 78.4933
2001-02-18 03:48 | 80.07 | 36940.1634 | 78.2833
2001-02-18 03:49 | 79.44 | 36940.1641 | 78.18
2001-02-18 03:50 | 79.12 | 36940.1648 | 78.0767
2001-02-18 03:51 | 79.12 | 36940.1655 | 77.8667
2001-02-18 03:52 | 78.81 | 36940.1662 | 77.6567
2001-02-18 03:53 | 78.81 | 36940.1669 | 77.4467
2001-02-18 03:54 | 78.49 | 36940.1676 | 77.4467
2001-02-18 03:55 | 78.18 | 36940.1683 | 77.3433
2001-02-18 03:56 | 78.18 | 36940.169 | 77.3433
2001-02-18 03:57 | 78.18 | 36940.1697 | 77.3433
2001-02-18 03:58 | 77.87 | 36940.1704 | 77.5533
2001-02-18 03:59 | 77.55 | 36940.1711 | 77.6567
2001-02-18 04:00 | 77.55 | 36940.1717 | 77.7633
2001-02-18 04:01 | 77.24 | 36940.1724 | 77.7633
2001-02-18 04:02 | 77.55 | 36940.1731 | 77.7633
2001-02-18 04:03 | 77.24 | 36940.1738 | 77.6567
2001-02-18 04:04 | 77.24 | 36940.1745 | 77.6567
2001-02-18 04:05 | 77.55 | 36940.1752 | 77.7633
2001-02-18 04:06 | 77.87 | 36940.1759 | 77.87
2001-02-18 04:07 | 77.55 | 36940.1766 | 77.87
2001-02-18 04:08 | 77.87 | 36940.1773 | 77.9733
2001-02-18 04:09 | 77.87 | 36940.178 | 78.0767
2001-02-18 04:10 | 77.55 | 36940.1787 | 78.18
2001-02-18 04:11 | 77.55 | 36940.1794 | 78.39
2001-02-18 04:12 | 77.87 | 36940.1801 | 78.6
2001-02-18 04:13 | 77.87 | 36940.1808 | 78.9133
2001-02-18 04:14 | 77.87 | 36940.1815 | 79.0167
2001-02-18 04:15 | 77.87 | 36940.1822 | 79.12
2001-02-18 04:16 | 78.18 | 36940.1829 | 79.12
2001-02-18 04:17 | 78.18 | 36940.1836 | 79.2267
2001-02-18 04:18 | 78.18 | 36940.1842 | 79.3333
2001-02-18 04:19 | 78.81 | 36940.1849 | 79.44
2001-02-18 04:20 | 78.81 | 36940.1856 | 79.44
2001-02-18 04:21 | 79.12 | 36940.1863 | 79.5433
2001-02-18 04:22 | 79.12 | 36940.187 | 79.7533
2001-02-18 04:23 | 79.12 | 36940.1877 | 80.1733
2001-02-18 04:24 | 79.12 | 36940.1884 | 80.3833
2001-02-18 04:25 | 79.44 | 36940.1891 | 80.5933
2001-02-18 04:26 | 79.44 | 36940.1898 | 80.5933
2001-02-18 04:27 | 79.44 | 36940.1905 | 81.02
2001-02-18 04:28 | 79.44 | 36940.1912 | 81.2333
2001-02-18 04:29 | 79.75 | 36940.1919 | 81.34
2001-02-18 04:30 | 80.07 | 36940.1926 | 81.8867
2001-02-18 04:31 | 80.7 | 36940.1933 | 82.65
2001-02-18 04:32 | 80.38 | 36940.194 | 83.85
2001-02-18 04:33 | 80.7 | 36940.1947 | 84.4
2001-02-18 04:34 | 80.7 | 36940.1954 | 84.73
2001-02-18 04:35 | 81.66 | 36940.1961 | 84.95
2001-02-18 04:36 | 81.34 | 36940.1967 | 84.95
2001-02-18 04:37 | 81.02 | 36940.1974 | 85.17
2001-02-18 04:38 | 83.3 | 36940.1981 | 84.95
2001-02-18 04:39 | 83.63 | 36940.1988 | 84.95
2001-02-18 04:40 | 84.62 | 36940.1995 | 84.84
2001-02-18 04:41 | 84.95 | 36940.2002 | 85.06
2001-02-18 04:42 | 84.62 | 36940.2009 | 85.06
2001-02-18 04:43 | 85.28 | 36940.2016 | 84.95
2001-02-18 04:44 | 84.95 | 36940.2023 | 84.73
2001-02-18 04:45 | 85.28 | 36940.203 | 84.51
2001-02-18 04:46 | 84.62 | 36940.2037 | 84.51
2001-02-18 04:47 | 84.95 | 36940.2044 | 84.4
2001-02-18 04:48 | 84.95 | 36940.2051 | 84.4
2001-02-18 04:49 | 85.28 | 36940.2058 | 84.29
2001-02-18 04:50 | 84.95 | 36940.2065 | 84.29
2001-02-18 04:51 | 84.62 | 36940.2072 | 84.29
2001-02-18 04:52 | 84.62 | 36940.2079 | 84.29
2001-02-18 04:53 | 84.29 | 36940.2086 | 84.29
2001-02-18 04:54 | 84.62 | 36940.2092 | 84.18
2001-02-18 04:55 | 84.29 | 36940.2099 | 84.07
2001-02-18 04:56 | 84.29 | 36940.2106 | 84.07
2001-02-18 04:57 | 84.29 | 36940.2113 | 84.07
2001-02-18 04:58 | 84.29 | 36940.212 | 84.18
2001-02-18 04:59 | 84.29 | 36940.2127 | 84.18
2001-02-18 05:00 | 84.29 | 36940.2134 | 84.18
2001-02-18 05:01 | 84.29 | 36940.2141 | 84.07
2001-02-18 05:02 | 83.96 | 36940.2148 | 83.96
2001-02-18 05:03 | 83.96 | 36940.2155 | 83.85
2001-02-18 05:04 | 84.29 | 36940.2162 | 83.85
2001-02-18 05:05 | 83.96 | 36940.2169 | 83.85
2001-02-18 05:06 | 84.29 | 36940.2176 | 83.96
2001-02-18 05:07 | 84.29 | 36940.2183 | 83.96
2001-02-18 05:08 | 83.96 | 36940.219 | 84.18
2001-02-18 05:09 | 83.96 | 36940.2197 | 84.4
2001-02-18 05:10 | 83.96 | 36940.2204 | 84.62
2001-02-18 05:11 | 83.63 | 36940.2211 | 84.62
2001-02-18 05:12 | 83.96 | 36940.2217 | 84.62
2001-02-18 05:13 | 83.96 | 36940.2224 | 84.73
2001-02-18 05:14 | 83.96 | 36940.2231 | 84.73
2001-02-18 05:15 | 83.96 | 36940.2238 | 84.73
2001-02-18 05:16 | 84.62 | 36940.2245 | 84.62
2001-02-18 05:17 | 84.62 | 36940.2252 | 84.29
2001-02-18 05:18 | 84.62 | 36940.2259 | 83.85
2001-02-18 05:19 | 84.62 | 36940.2266 | 83.52
2001-02-18 05:20 | 84.62 | 36940.2273 | 83.63
2001-02-18 05:21 | 84.95 | 36940.228 | 83.85
2001-02-18 05:22 | 84.62 | 36940.2287 | 83.85
2001-02-18 05:23 | 84.62 | 36940.2294 | 83.74
2001-02-18 05:24 | 84.62 | 36940.2301 | 83.74
2001-02-18 05:25 | 83.63 | 36940.2308 | 84.07
2001-02-18 05:26 | 83.3 | 36940.2315 | 84.4
2001-02-18 05:27 | 83.63 | 36940.2322 | 84.84
2001-02-18 05:28 | 83.96 | 36940.2329 | 84.95
2001-02-18 05:29 | 83.96 | 36940.2336 | 84.95
2001-02-18 05:30 | 83.63 | 36940.2342 | 84.73
2001-02-18 05:31 | 83.63 | 36940.2349 | 84.62
2001-02-18 05:32 | 83.96 | 36940.2356 | 84.62
2001-02-18 05:33 | 84.62 | 36940.2363 | 84.62
2001-02-18 05:34 | 84.62 | 36940.237 | 84.62
2001-02-18 05:35 | 85.28 | 36940.2377 | 84.62
2001-02-18 05:36 | 84.95 | 36940.2384 | 84.51
2001-02-18 05:37 | 84.62 | 36940.2391 | 84.4
2001-02-18 05:38 | 84.62 | 36940.2398 | 84.29
2001-02-18 05:39 | 84.62 | 36940.2405 | 84.29
2001-02-18 05:40 | 84.62 | 36940.2412 | 84.29
2001-02-18 05:41 | 84.62 | 36940.2419 | 84.29
2001-02-18 05:42 | 84.62 | 36940.2426 | 84.29
2001-02-18 05:43 | 84.62 | 36940.2433 | 84.62
2001-02-18 05:44 | 84.29 | 36940.244 | 84.95
2001-02-18 05:45 | 84.29 | 36940.2447 | 85.28
2001-02-18 05:46 | 84.29 | 36940.2454 | 85.28
2001-02-18 05:47 | 84.29 | 36940.2461 | 85.3933
2001-02-18 05:48 | 84.29 | 36940.2467 | 85.5067
2001-02-18 05:49 | 84.29 | 36940.2474 | 85.62
2001-02-18 05:50 | 84.29 | 36940.2481 | 85.62
2001-02-18 05:51 | 85.28 | 36940.2488 | 85.5067
2001-02-18 05:52 | 85.28 | 36940.2495 | 85.3933
2001-02-18 05:53 | 85.28 | 36940.2502 | 85.28
2001-02-18 05:54 | 85.28 | 36940.2509 | 85.28
2001-02-18 05:55 | 85.62 | 36940.2516 | 84.95
2001-02-18 05:56 | 85.62 | 36940.2523 | 84.51
2001-02-18 05:57 | 85.62 | 36940.253 | 84.29
2001-02-18 05:58 | 85.62 | 36940.2537 | 84.29
2001-02-18 05:59 | 85.28 | 36940.2544 | 84.4
2001-02-18 06:00 | 85.28 | 36940.2551 | 84.4
2001-02-18 06:01 | 85.28 | 36940.2558 | 84.51
2001-02-18 06:02 | 85.28 | 36940.2565 | 84.62
2001-02-18 06:03 | 84.29 | 36940.2572 | 84.62
2001-02-18 06:04 | 83.96 | 36940.2579 | 84.62
2001-02-18 06:05 | 84.62 | 36940.2586 | 84.73
2001-02-18 06:06 | 84.29 | 36940.2592 | 84.73
2001-02-18 06:07 | 84.29 | 36940.2599 | 84.73
2001-02-18 06:08 | 84.62 | 36940.2606 | 84.73
2001-02-18 06:09 | 84.62 | 36940.2613 | 84.84
2001-02-18 06:10 | 84.62 | 36940.262 | 84.95
2001-02-18 06:11 | 84.62 | 36940.2627 | 84.84
2001-02-18 06:12 | 84.62 | 36940.2634 | 84.84
2001-02-18 06:13 | 84.95 | 36940.2641 | 84.84
2001-02-18 06:14 | 84.62 | 36940.2648 | 84.95
2001-02-18 06:15 | 84.62 | 36940.2655 | 84.95
2001-02-18 06:16 | 84.95 | 36940.2662 | 84.95
2001-02-18 06:17 | 84.95 | 36940.2669 | 84.95
2001-02-18 06:18 | 84.95 | 36940.2676 | 84.95
2001-02-18 06:19 | 84.62 | 36940.2683 | 84.95
2001-02-18 06:20 | 84.95 | 36940.269 | 84.95
2001-02-18 06:21 | 84.95 | 36940.2697 | 84.95
2001-02-18 06:22 | 84.95 | 36940.2704 | 84.95
2001-02-18 06:23 | 84.95 | 36940.2711 | 84.95
2001-02-18 06:24 | 84.95 | 36940.2717 | 84.95
2001-02-18 06:25 | 84.95 | 36940.2724 | 85.1733
2001-02-18 06:26 | 84.95 | 36940.2731 | 85.2833
2001-02-18 06:27 | 84.95 | 36940.2738 | 85.5067
2001-02-18 06:28 | 84.95 | 36940.2745 | 85.5067
2001-02-18 06:29 | 84.95 | 36940.2752 | 85.62
2001-02-18 06:30 | 84.95 | 36940.2759 | 85.62
2001-02-18 06:31 | 84.95 | 36940.2766 | 85.62
2001-02-18 06:32 | 84.95 | 36940.2773 | 85.62
2001-02-18 06:33 | 85.62 | 36940.278 | 85.73
2001-02-18 06:34 | 85.28 | 36940.2787 | 85.6167
2001-02-18 06:35 | 85.62 | 36940.2794 | 85.5033
2001-02-18 06:36 | 85.62 | 36940.2801 | 85.28
2001-02-18 06:37 | 85.62 | 36940.2808 | 85.3933
2001-02-18 06:38 | 85.62 | 36940.2815 | 85.9533
2001-02-18 06:39 | 85.62 | 36940.2822 | 86.6267
2001-02-18 06:40 | 85.62 | 36940.2829 | 87.3
2001-02-18 06:41 | 85.95 | 36940.2836 | 88.1033
2001-02-18 06:42 | 85.28 | 36940.2842 | 89.0267
2001-02-18 06:43 | 85.28 | 36940.2849 | 91.2667
2001-02-18 06:44 | 85.28 | 36940.2856 | 92.0833
2001-02-18 06:45 | 85.62 | 36940.2863 | 93.5133
2001-02-18 06:46 | 86.96 | 36940.287 | 93.6367
2001-02-18 06:47 | 87.3 | 36940.2877 | 95.35
2001-02-18 06:48 | 87.64 | 36940.2884 | 96.7233
2001-02-18 06:49 | 89.37 | 36940.2891 | 98.1
2001-02-18 06:50 | 90.07 | 36940.2898 | 98.6067
2001-02-18 06:51 | 94.36 | 36940.2905 | 98.6067
2001-02-18 06:52 | 91.82 | 36940.2912 | 98.3533
2001-02-18 06:53 | 94.36 | 36940.2919 | 98.1
2001-02-18 06:54 | 94.73 | 36940.2926 | 97.8467
2001-02-18 06:55 | 96.96 | 36940.2933 | 97.8467
2001-02-18 06:56 | 98.48 | 36940.294 | 97.5933
2001-02-18 06:57 | 98.86 | 36940.2947 | 97.2167
2001-02-18 06:58 | 98.48 | 36940.2954 | 96.0933
2001-02-18 06:59 | 98.48 | 36940.2961 | 95.72
2001-02-18 07:00 | 98.1 | 36940.2967 | 95.72
2001-02-18 07:01 | 97.72 | 36940.2974 | 95.8433
2001-02-18 07:02 | 97.72 | 36940.2981 | 95.2267
2001-02-18 07:03 | 98.1 | 36940.2988 | 94.1167
2001-02-18 07:04 | 96.96 | 36940.2995 | 93.3833
2001-02-18 07:05 | 96.59 | 36940.3002 | 93.02
2001-02-18 07:06 | 94.73 | 36940.3009 | 92.9
2001-02-18 07:07 | 95.84 | 36940.3016 | 92.9
2001-02-18 07:08 | 96.59 | 36940.3023 | 92.9
2001-02-18 07:09 | 95.1 | 36940.303 | 92.9
2001-02-18 07:10 | 93.99 | 36940.3037 | 92.9
2001-02-18 07:11 | 93.26 | 36940.3044 | 92.78
2001-02-18 07:12 | 92.9 | 36940.3051 | 92.42
2001-02-18 07:13 | 92.9 | 36940.3058 | 91.8267
2001-02-18 07:14 | 92.9 | 36940.3065 | 91.2367
2001-02-18 07:15 | 92.9 | 36940.3072 | 90.77
2001-02-18 07:16 | 92.9 | 36940.3079 | 90.5367
2001-02-18 07:17 | 92.9 | 36940.3086 | 90.42
2001-02-18 07:18 | 92.9 | 36940.3092 | 90.1867
2001-02-18 07:19 | 92.54 | 36940.3099 | 89.9533
2001-02-18 07:20 | 91.82 | 36940.3106 | 89.6033
2001-02-18 07:21 | 91.12 | 36940.3113 | 89.4867
2001-02-18 07:22 | 90.77 | 36940.312 | 89.14
2001-02-18 07:23 | 90.42 | 36940.3127 | 88.7933
2001-02-18 07:24 | 90.42 | 36940.3134 | 88.5633
2001-02-18 07:25 | 90.42 | 36940.3141 | 88.5633
2001-02-18 07:26 | 89.72 | 36940.3148 | 88.5633
2001-02-18 07:27 | 89.72 | 36940.3155 | 88.4467
2001-02-18 07:28 | 89.37 | 36940.3162 | 88.33
2001-02-18 07:29 | 89.37 | 36940.3169 | 88.2167
2001-02-18 07:30 | 88.68 | 36940.3176 | 88.1033
2001-02-18 07:31 | 88.33 | 36940.3183 | 87.99
2001-02-18 07:32 | 88.68 | 36940.319 | 88.1033
2001-02-18 07:33 | 88.68 | 36940.3197 | 88.1033
2001-02-18 07:34 | 88.33 | 36940.3204 | 88.1033
2001-02-18 07:35 | 88.33 | 36940.3211 | 87.99
2001-02-18 07:36 | 88.33 | 36940.3217 | 87.99
2001-02-18 07:37 | 87.99 | 36940.3224 | 87.99
2001-02-18 07:38 | 87.99 | 36940.3231 | 87.6467
2001-02-18 07:39 | 87.99 | 36940.3238 | 87.3033
2001-02-18 07:40 | 88.33 | 36940.3245 | 87.0733
2001-02-18 07:41 | 87.99 | 36940.3252 | 86.96
2001-02-18 07:42 | 87.99 | 36940.3259 | 86.8467
2001-02-18 07:43 | 87.99 | 36940.3266 | 86.51
2001-02-18 07:44 | 87.99 | 36940.3273 | 86.1767
2001-02-18 07:45 | 87.99 | 36940.328 | 85.73
2001-02-18 07:46 | 86.96 | 36940.3287 | 85.2833
2001-02-18 07:47 | 86.96 | 36940.3294 | 85.17
2001-02-18 07:48 | 87.3 | 36940.3301 | 85.2833
2001-02-18 07:49 | 86.62 | 36940.3308 | 85.5067
2001-02-18 07:50 | 86.62 | 36940.3315 | 85.62
2001-02-18 07:51 | 86.29 | 36940.3322 | 85.73
2001-02-18 07:52 | 85.62 | 36940.3329 | 85.84
2001-02-18 07:53 | 85.28 | 36940.3336 | 85.95
2001-02-18 07:54 | 84.95 | 36940.3342 | 85.95
2001-02-18 07:55 | 85.28 | 36940.3349 | 85.95
2001-02-18 07:56 | 85.62 | 36940.3356 | 85.95
2001-02-18 07:57 | 85.62 | 36940.3363 | 86.0633
2001-02-18 07:58 | 85.62 | 36940.337 | 86.1767
2001-02-18 07:59 | 85.95 | 36940.3377 | 86.1767
2001-02-18 08:00 | 85.95 | 36940.3384 | 86.0633
2001-02-18 08:01 | 85.95 | 36940.3391 | 85.84
2001-02-18 08:02 | 85.95 | 36940.3398 | 85.73
2001-02-18 08:03 | 85.95 | 36940.3405 | 85.62
2001-02-18 08:04 | 85.95 | 36940.3412 | 85.73
2001-02-18 08:05 | 86.29 | 36940.3419 | 85.84
2001-02-18 08:06 | 86.29 | 36940.3426 | 85.84
2001-02-18 08:07 | 85.95 | 36940.3433 | 85.73
2001-02-18 08:08 | 85.95 | 36940.344 | 85.73
2001-02-18 08:09 | 85.62 | 36940.3447 | 85.84
2001-02-18 08:10 | 85.62 | 36940.3454 | 85.95
2001-02-18 08:11 | 85.62 | 36940.3461 | 85.95
2001-02-18 08:12 | 85.95 | 36940.3467 | 85.84
2001-02-18 08:13 | 85.95 | 36940.3474 | 85.73
2001-02-18 08:14 | 85.62 | 36940.3481 | 85.62
2001-02-18 08:15 | 85.62 | 36940.3488 | 85.62
2001-02-18 08:16 | 85.95 | 36940.3495 | 85.62
2001-02-18 08:17 | 85.95 | 36940.3502 | 85.62
2001-02-18 08:18 | 85.95 | 36940.3509 | 85.73
2001-02-18 08:19 | 85.95 | 36940.3516 | 85.84
2001-02-18 08:20 | 85.62 | 36940.3523 | 85.95
2001-02-18 08:21 | 85.62 | 36940.353 | 85.95
2001-02-18 08:22 | 85.62 | 36940.3537 | 85.95
2001-02-18 08:23 | 85.62 | 36940.3544 | 85.95
2001-02-18 08:24 | 85.62 | 36940.3551 | 85.95
2001-02-18 08:25 | 85.62 | 36940.3558 | 86.0633
2001-02-18 08:26 | 85.95 | 36940.3565 | 86.1767
2001-02-18 08:27 | 85.95 | 36940.3572 | 86.4
2001-02-18 08:28 | 85.95 | 36940.3579 | 86.51
2001-02-18 08:29 | 85.95 | 36940.3586 | 86.62
2001-02-18 08:30 | 85.95 | 36940.3592 | 86.62
2001-02-18 08:31 | 85.95 | 36940.3599 | 86.62
2001-02-18 08:32 | 85.95 | 36940.3606 | 86.0633
2001-02-18 08:33 | 86.29 | 36940.3613 | 86.0633
2001-02-18 08:34 | 86.29 | 36940.362 | 86.0633
2001-02-18 08:35 | 86.62 | 36940.3627 | 86.62
2001-02-18 08:36 | 86.62 | 36940.3634 | 86.62
2001-02-18 08:37 | 86.62 | 36940.3641 | 86.51
2001-02-18 08:38 | 86.62 | 36940.3648 | 86.51
2001-02-18 08:39 | 86.62 | 36940.3655 | 86.4
2001-02-18 08:40 | 84.95 | 36940.3662 | 86.4
2001-02-18 08:41 | 86.62 | 36940.3669 | 86.29
2001-02-18 08:42 | 86.62 | 36940.3676 | 86.29
2001-02-18 08:43 | 86.62 | 36940.3683 | 86.29
2001-02-18 08:44 | 86.62 | 36940.369 | 86.29
2001-02-18 08:45 | 86.29 | 36940.3697 | 86.4
2001-02-18 08:46 | 86.62 | 36940.3704 | 86.51
2001-02-18 08:47 | 86.29 | 36940.3711 | 86.62
2001-02-18 08:48 | 86.29 | 36940.3717 | 87.0767
2001-02-18 08:49 | 86.29 | 36940.3724 | 87.9933
2001-02-18 08:50 | 86.29 | 36940.3731 | 89.26
2001-02-18 08:51 | 86.29 | 36940.3738 | 90.07
2001-02-18 08:52 | 86.29 | 36940.3745 | 90.42
2001-02-18 08:53 | 86.62 | 36940.3752 | 90.3033
2001-02-18 08:54 | 86.62 | 36940.3759 | 91.3733
2001-02-18 08:55 | 86.62 | 36940.3766 | 93.3033
2001-02-18 08:56 | 87.99 | 36940.3773 | 95.2267
2001-02-18 08:57 | 89.37 | 36940.378 | 95.84
2001-02-18 08:58 | 90.42 | 36940.3787 | 95.3467
2001-02-18 08:59 | 90.42 | 36940.3794 | 94.8533
2001-02-18 09:00 | 90.42 | 36940.3801 | 94.24
2001-02-18 09:01 | 90.07 | 36940.3808 | 93.39
2001-02-18 09:02 | 93.63 | 36940.3815 | 92.6633
2001-02-18 09:03 | 96.21 | 36940.3822 | 92.06
2001-02-18 09:04 | 95.84 | 36940.3829 | 91.59
2001-02-18 09:05 | 95.47 | 36940.3836 | 90.77
2001-02-18 09:06 | 94.73 | 36940.3842 | 89.84
2001-02-18 09:07 | 94.36 | 36940.3849 | 89.0267
2001-02-18 09:08 | 93.63 | 36940.3856 | 87.8833
2001-02-18 09:09 | 92.18 | 36940.3863 | 86.1933
2001-02-18 09:10 | 92.18 | 36940.387 | 84.2967
2001-02-18 09:11 | 91.82 | 36940.3877 | 82.7533
2001-02-18 09:12 | 90.77 | 36940.3884 | 81.88
2001-02-18 09:13 | 89.72 | 36940.3891 | 81.34
2001-02-18 09:14 | 89.03 | 36940.3898 | 81.2333
2001-02-18 09:15 | 88.33 | 36940.3905 | 81.34
2001-02-18 09:16 | 86.29 | 36940.3912 | 81.4467
2001-02-18 09:17 | 83.96 | 36940.3919 | 81.34
2001-02-18 09:18 | 82.64 | 36940.3926 | 81.1267
2001-02-18 09:19 | 81.66 | 36940.3933 | 80.8067
2001-02-18 09:20 | 81.34 | 36940.394 | 80.8067
2001-02-18 09:21 | 81.02 | 36940.3947 | 81.02
2001-02-18 09:22 | 81.34 | 36940.3954 | 81.8833
2001-02-18 09:23 | 81.66 | 36940.3961 | 82.7533
2001-02-18 09:24 | 81.34 | 36940.3967 | 83.52
2001-02-18 09:25 | 81.02 | 36940.3974 | 83.85
2001-02-18 09:26 | 81.02 | 36940.3981 | 83.63
2001-02-18 09:27 | 80.38 | 36940.3988 | 83.41
2001-02-18 09:28 | 81.02 | 36940.3995 | 82.97
2001-02-18 09:29 | 81.66 | 36940.4002 | 82.86
2001-02-18 09:30 | 82.97 | 36940.4009 | 82.53
2001-02-18 09:31 | 83.63 | 36940.4016 | 82.53
2001-02-18 09:32 | 83.96 | 36940.4023 | 82.42
2001-02-18 09:33 | 83.96 | 36940.403 | 82.2033
2001-02-18 09:34 | 82.97 | 36940.4037 | 82.0933
2001-02-18 09:35 | 83.3 | 36940.4044 | 82.0933
2001-02-18 09:36 | 82.64 | 36940.4051 | 82.53
2001-02-18 09:37 | 82.64 | 36940.4058 | 83.19
2001-02-18 09:38 | 82.31 | 36940.4065 | 84.4033
2001-02-18 09:39 | 82.64 | 36940.4072 | 85.51
2001-02-18 09:40 | 82.31 | 36940.4079 | 86.0633
2001-02-18 09:41 | 81.66 | 36940.4086 | 86.1767
2001-02-18 09:42 | 82.31 | 36940.4092 | 86.7433
2001-02-18 09:43 | 82.31 | 36940.4099 | 88.2333
2001-02-18 09:44 | 82.97 | 36940.4106 | 90.1967
2001-02-18 09:45 | 84.29 | 36940.4113 | 91.5933
2001-02-18 09:46 | 85.95 | 36940.412 | 91.9433
2001-02-18 09:47 | 86.29 | 36940.4127 | 91.9433
2001-02-18 09:48 | 85.95 | 36940.4134 | 92.1833
2001-02-18 09:49 | 86.29 | 36940.4141 | 92.54
2001-02-18 09:50 | 87.99 | 36940.4148 | 92.54
2001-02-18 09:51 | 90.42 | 36940.4155 | 91.83
2001-02-18 09:52 | 92.18 | 36940.4162 | 91.1233
2001-02-18 09:53 | 92.18 | 36940.4169 | 90.77
2001-02-18 09:54 | 91.47 | 36940.4176 | 91.12
2001-02-18 09:55 | 92.18 | 36940.4183 | 91.2367
2001-02-18 09:56 | 92.9 | 36940.419 | 90.6533
2001-02-18 09:57 | 92.54 | 36940.4197 | 89.1467
2001-02-18 09:58 | 92.18 | 36940.4204 | 87.8767
2001-02-18 09:59 | 90.77 | 36940.4211 | 86.6267
2001-02-18 10:00 | 90.42 | 36940.4217 | 85.5133
2001-02-18 10:01 | 91.12 | 36940.4224 | 84.7333
2001-02-18 10:02 | 91.82 | 36940.4231 | 84.29
2001-02-18 10:03 | 90.77 | 36940.4238 | 84.29
2001-02-18 10:04 | 89.37 | 36940.4245 | 83.85
2001-02-18 10:05 | 87.3 | 36940.4252 | 83.63
2001-02-18 10:06 | 86.96 | 36940.4259 | 83.3
2001-02-18 10:07 | 85.62 | 36940.4266 | 83.08
2001-02-18 10:08 | 83.96 | 36940.4273 | 82.86
2001-02-18 10:09 | 84.62 | 36940.428 | 83.08
2001-02-18 10:10 | 84.29 | 36940.4287 | 83.52
2001-02-18 10:11 | 83.96 | 36940.4294 | 83.74
2001-02-18 10:12 | 83.3 | 36940.4301 | 83.63
2001-02-18 10:13 | 83.63 | 36940.4308 | 83.52
2001-02-18 10:14 | 82.97 | 36940.4315 | 83.63
2001-02-18 10:15 | 82.64 | 36940.4322 | 83.85
2001-02-18 10:16 | 82.97 | 36940.4329 | 83.74
2001-02-18 10:17 | 83.63 | 36940.4336 | 83.63
2001-02-18 10:18 | 83.96 | 36940.4342 | 83.85
2001-02-18 10:19 | 83.63 | 36940.4349 | 84.4
2001-02-18 10:20 | 83.3 | 36940.4356 | 84.95
2001-02-18 10:21 | 83.63 | 36940.4363 | 84.95
2001-02-18 10:22 | 83.96 | 36940.437 | 84.84
2001-02-18 10:23 | 83.96 | 36940.4377 | 84.62
2001-02-18 10:24 | 83.3 | 36940.4384 | 84.62
2001-02-18 10:25 | 83.63 | 36940.4391 | 84.51
2001-02-18 10:26 | 84.62 | 36940.4398 | 84.29
2001-02-18 10:27 | 84.95 | 36940.4405 | 84.07
2001-02-18 10:28 | 85.28 | 36940.4412 | 83.96
2001-02-18 10:29 | 84.62 | 36940.4419 | 83.85
2001-02-18 10:30 | 84.62 | 36940.4426 | 83.41
2001-02-18 10:31 | 84.62 | 36940.4433 | 83.08
2001-02-18 10:32 | 84.62 | 36940.444 | 82.86
2001-02-18 10:33 | 84.29 | 36940.4447 | 83.08
2001-02-18 10:34 | 83.96 | 36940.4454 | 83.08
2001-02-18 10:35 | 83.96 | 36940.4461 | 83.08
2001-02-18 10:36 | 83.96 | 36940.4467 | 82.86
2001-02-18 10:37 | 83.63 | 36940.4474 | 82.97
2001-02-18 10:38 | 82.64 | 36940.4481 | 83.41
2001-02-18 10:39 | 82.97 | 36940.4488 | 84.4033
2001-02-18 10:40 | 82.97 | 36940.4495 | 84.9533
2001-02-18 10:41 | 83.3 | 36940.4502 | 85.62
2001-02-18 10:42 | 82.97 | 36940.4509 | 85.8433
2001-02-18 10:43 | 82.97 | 36940.4516 | 86.6267
2001-02-18 10:44 | 82.64 | 36940.4523 | 87.1933
2001-02-18 10:45 | 83.3 | 36940.453 | 87.99
2001-02-18 10:46 | 84.29 | 36940.4537 | 88.3333
2001-02-18 10:47 | 85.62 | 36940.4544 | 88.68
2001-02-18 10:48 | 84.95 | 36940.4551 | 88.7967
2001-02-18 10:49 | 86.29 | 36940.4558 | 89.03
2001-02-18 10:50 | 86.29 | 36940.4565 | 88.7967
2001-02-18 10:51 | 87.3 | 36940.4572 | 88.22
2001-02-18 10:52 | 87.99 | 36940.4579 | 87.0833
2001-02-18 10:53 | 88.68 | 36940.4586 | 85.9567
2001-02-18 10:54 | 88.33 | 36940.4592 | 85.1733
2001-02-18 10:55 | 89.03 | 36940.4599 | 84.62
2001-02-18 10:56 | 89.03 | 36940.4606 | 83.96
2001-02-18 10:57 | 89.03 | 36940.4613 | 82.9733
2001-02-18 10:58 | 88.33 | 36940.462 | 82.2067
2001-02-18 10:59 | 87.3 | 36940.4627 | 81.88
2001-02-18 11:00 | 85.62 | 36940.4634 | 81.9867
2001-02-18 11:01 | 84.95 | 36940.4641 | 82.2033
2001-02-18 11:02 | 84.95 | 36940.4648 | 82.31
2001-02-18 11:03 | 83.96 | 36940.4655 | 82.97
2001-02-18 11:04 | 82.97 | 36940.4662 | 83.85
2001-02-18 11:05 | 81.99 | 36940.4669 | 84.84
2001-02-18 11:06 | 81.66 | 36940.4676 | 85.2833
2001-02-18 11:07 | 81.99 | 36940.4683 | 85.5067
2001-02-18 11:08 | 82.31 | 36940.469 | 85.3967
2001-02-18 11:09 | 82.31 | 36940.4697 | 86.07
2001-02-18 11:10 | 82.31 | 36940.4704 | 87.67
2001-02-18 11:11 | 84.29 | 36940.4711 | 89.61
2001-02-18 11:12 | 84.95 | 36940.4717 | 90.6533
2001-02-18 11:13 | 85.28 | 36940.4724 | 90.6533
2001-02-18 11:14 | 85.62 | 36940.4731 | 90.6533
2001-02-18 11:15 | 85.62 | 36940.4738 | 90.6533
2001-02-18 11:16 | 84.95 | 36940.4745 | 90.6533
2001-02-18 11:17 | 87.64 | 36940.4752 | 90.42
2001-02-18 11:18 | 90.42 | 36940.4759 | 89.7233
2001-02-18 11:19 | 90.77 | 36940.4766 | 88.7967
2001-02-18 11:20 | 90.77 | 36940.4773 | 87.6467
2001-02-18 11:21 | 90.42 | 36940.478 | 87.0733
2001-02-18 11:22 | 90.77 | 36940.4787 | 86.8467
2001-02-18 11:23 | 90.77 | 36940.4794 | 86.29
2001-02-18 11:24 | 90.42 | 36940.4801 | 85.4
2001-02-18 11:25 | 90.07 | 36940.4808 | 84.73
2001-02-18 11:26 | 88.68 | 36940.4815 | 85.0633
2001-02-18 11:27 | 87.64 | 36940.4822 | 85.6167
2001-02-18 11:28 | 86.62 | 36940.4829 | 85.84
2001-02-18 11:29 | 86.96 | 36940.4836 | 85.84
2001-02-18 11:30 | 86.96 | 36940.4842 | 85.9533
2001-02-18 11:31 | 84.95 | 36940.4849 | 86.2867
2001-02-18 11:32 | 84.29 | 36940.4856 | 86.1767
2001-02-18 11:33 | 84.95 | 36940.4863 | 85.9533
2001-02-18 11:34 | 85.95 | 36940.487 | 85.3967
2001-02-18 11:35 | 85.95 | 36940.4877 | 85.3967
2001-02-18 11:36 | 85.62 | 36940.4884 | 85.2833
2001-02-18 11:37 | 85.95 | 36940.4891 | 85.2833
2001-02-18 11:38 | 86.29 | 36940.4898 | 84.73
2001-02-18 11:39 | 86.62 | 36940.4905 | 84.4
2001-02-18 11:40 | 85.62 | 36940.4912 | 83.96
2001-02-18 11:41 | 85.62 | 36940.4919 | 83.74
2001-02-18 11:42 | 84.95 | 36940.4926 | 83.52
2001-02-18 11:43 | 85.62 | 36940.4933 | 83.63
2001-02-18 11:44 | 85.28 | 36940.494 | 83.85
2001-02-18 11:45 | 84.95 | 36940.4947 | 83.85
2001-02-18 11:46 | 83.96 | 36940.4954 | 83.85
2001-02-18 11:47 | 84.29 | 36940.4961 | 84.29
2001-02-18 11:48 | 83.63 | 36940.4967 | 85.4807
2001-02-18 11:49 | 83.3 |  | 87.2189
2001-02-18 11:50 | 83.63 |  | 33.2189
2001-02-18 11:51 | 83.96
2001-02-18 11:52 | 83.96
2001-02-18 11:53 | 83.63
2001-02-18 11:54 | 83.96
2001-02-18 11:55 | 85.28
87.2022
33.2022

## Washing Machine Data
Date | Time | Temperature | Graph times | Temperature
2001-01-14 | 19:23 | 96.73 | 16:25 | 96.73 |  | 17:25
2001-01-14 | 19:28 | 104.02 | 16:30 | 104.02 |  | 17:30
2001-01-14 | 19:33 | 98.15 | 16:35 | 98.15 |  | 17:35
2001-01-14 | 19:38 | 93.92 | 16:40 | 93.92 |  | 17:40
2001-01-14 | 19:43 | 83.79 | 16:45 | 83.79 |  | 17:45
2001-01-14 | 19:48 | 73.47 | 16:50 | 73.47 |  | 17:50
2001-01-14 | 19:53 | 73.47 | 16:55 | 73.47 |  | 17:55
2001-01-14 | 19:58 | 72.83 | 17:00 | 72.83 |  | 18:00
2001-01-14 | 20:03 | 73.47 | 17:05 | 73.47 |  | 18:05
2001-01-14 | 20:08 | 93.22 | 17:10 | 93.22 |  | 18:10
2001-01-14 | 20:13 | 100.32 | 17:15 | 100.32 |  | 18:15
2001-01-14 | 20:18 | 90.47 | 17:20 | 90.47 |  | 18:20
2001-01-14 | 20:23 | 77.97 | 17:25 | 77.97
2001-01-14 | 20:28 | 83.13 | 17:30 | 83.13
2001-01-14 | 20:33 | 90.47 | 17:35 | 90.47
2001-01-14 | 20:38 | 75.39 | 17:40 | 75.39
2001-01-14 | 20:43 | 72.83 | 17:45 | 72.83
2001-01-14 | 20:48 | 73.47 | 17:50 | 73.47
2001-01-14 | 20:53 | 80.54 | 17:55 | 80.54
2001-01-14 | 20:58 | 97.44 | 18:00 | 97.44
2001-01-14 | 21:03 | 104.78 | 18:05 | 104.78
2001-01-14 | 21:08 | 101.79 | 18:10 | 101.79
2001-01-14 | 21:13 | 82.48 | 18:15 | 82.48
2001-01-14 | 21:18 | 95.31 | 18:20 | 95.31
2001-01-14 | 21:23 | 99.59 | 18:25 | 99.59
2001-01-14 | 21:28 | 93.92 | 18:30 | 93.92
2001-01-14 | 21:33 | 87.77 | 18:35 | 87.77
2001-01-14 | 21:38 | 92.53 | 18:40 | 92.53
2001-01-14 | 21:43 | 105.54 | 18:45 | 105.54
2001-01-14 | 21:48 | 96.02 | 18:50 | 96.02
2001-01-14 | 21:53 | 107.86 | 18:55 | 107.86
2001-01-14 | 21:58 | 78.61 | 19:00 | 78.61
2001-01-14 | 22:03 | 71.57 | 19:05 | 71.57
2001-01-14 | 22:08 | 74.74 | 19:10 | 74.74
2001-01-14 | 22:13 | 76.03 | 19:15 | 76.03
2001-01-14 | 22:18 | 76.03 | 19:20 | 76.03
2001-01-14 | 22:23 | 76.03 | 19:25 | 76.03
2001-01-14 | 22:28 | 79.25 | 19:30 | 79.25
2001-01-14 | 22:33 | 104.78 | 19:35 | 104.78
2001-01-14 | 22:38 | 98.15 | 19:40 | 98.15
2001-01-14 | 22:43 | 103.27 | 19:45 | 103.27
2001-01-14 | 22:48 | 80.54 | 19:50 | 80.54
2001-01-14 | 22:53 | 91.84 | 19:55 | 91.84
2001-01-14 | 22:58 | 84.45 | 20:00 | 84.45
2001-01-14 | 23:03 | 74.1 | 20:05 | 74.1
2001-01-14 | 23:08 | 83.79 | 20:10 | 83.79
2001-01-14 | 23:13 | 97.44 | 20:15 | 97.44
2001-01-14 | 23:18 | 96.73 | 20:20 | 96.73
2001-01-14 | 23:23 | 91.16 | 20:25 | 91.16
2001-01-14 | 23:28 | 74.1 | 20:30 | 74.1
2001-01-14 | 23:33 | 75.39 | 20:35 | 75.39
2001-01-14 | 23:38 | 75.39 | 20:40 | 75.39
2001-01-14 | 23:43 | 76.03 | 20:45 | 76.03
2001-01-14 | 23:48 | 76.03 | 20:50 | 76.03
2001-01-14 | 23:53 | 76.03 | 20:55 | 76.03
2001-01-14 | 23:58 | 75.39 | 21:00 | 75.39
2001-01-15 | 0:03 | 75.39 | 21:05 | 75.39 | 0:05
2001-01-15 | 0:08 | 75.39 | 21:10 | 75.39
2001-01-15 | 0:13 | 75.39 | 21:15 | 75.39
2001-01-15 | 0:18 | 74.74 | 21:20 | 74.74
2001-01-15 | 0:23 | 74.74 | 21:25 | 74.74
2001-01-15 | 0:28 | 74.74 | 21:30 | 74.74
2001-01-15 | 0:33 | 74.74 | 21:35 | 74.74
2001-01-15 | 0:38 | 74.74 | 21:40 | 74.74
2001-01-15 | 0:43 | 110.24 | 21:45 | 110.24
2001-01-15 | 0:48 | 104.02 | 21:50 | 104.02
2001-01-15 | 0:53 | 107.08 | 21:55 | 107.08
2001-01-15 | 0:58 | 89.12 | 22:00 | 89.12
2001-01-15 | 1:03 | 68.44 | 22:05 | 68.44
2001-01-15 | 1:08 | 70.32 | 22:10 | 70.32
2001-01-15 | 1:13 | 72.83 | 22:15 | 72.83
2001-01-15 | 1:18 | 73.47 | 22:20 | 73.47
2001-01-15 | 1:23 | 74.1 | 22:25 | 74.1
2001-01-15 | 1:28 | 74.1 | 22:30 | 74.1
2001-01-15 | 1:33 | 73.47 | 22:35 | 73.47
2001-01-15 | 1:38 | 73.47 | 22:40 | 73.47
2001-01-15 | 1:43 | 72.83 | 22:45 | 72.83
2001-01-15 | 1:48 | 73.47 | 22:50 | 73.47
2001-01-15 | 1:53 | 73.47 | 22:55 | 73.47
2001-01-15 | 1:58 | 74.1 | 23:00 | 74.1
2001-01-15 | 2:03 | 74.1 | 23:05 | 74.1
2001-01-15 | 2:08 | 74.1 | 23:10 | 74.1
2001-01-15 | 2:13 | 74.1 | 23:15 | 74.1
2001-01-15 | 2:18 | 74.1 | 23:20 | 74.1
2001-01-15 | 2:23 | 74.1 | 23:25 | 74.1
2001-01-15 | 2:28 | 74.1 | 23:30 | 74.1
2001-01-15 | 2:33 | 74.1 | 23:35 | 74.1
2001-01-15 | 2:38 | 74.1 | 23:40 | 74.1
2001-01-15 | 2:43 | 73.47 | 23:45 | 73.47
2001-01-15 | 2:48 | 73.47 | 23:50 | 73.47
2001-01-15 | 2:53 | 73.47 | 23:55 | 73.47
2001-01-15 | 2:58 | 73.47 | 0:00 | 73.47
2001-01-15 | 3:03 | 73.47 | 0:05 | 73.47
2001-01-15 | 3:08 | 73.47 | 0:10 | 73.47
2001-01-15 | 3:13 | 72.83 | 0:15 | 72.83
2001-01-15 | 3:18 | 72.83 | 0:20 | 72.83
2001-01-15 | 3:23 | 72.83 | 0:25 | 72.83
2001-01-15 | 3:28 | 72.83 | 0:30 | 72.83
2001-01-15 | 3:33 | 72.83 | 0:35 | 72.83
2001-01-15 | 3:38 | 72.83 | 0:40 | 72.83
2001-01-15 | 3:43 | 72.83 | 0:45 | 72.83
2001-01-15 | 3:48 | 72.83 | 0:50 | 72.83
2001-01-15 | 3:53 | 72.83 | 0:55 | 72.83
2001-01-15 | 3:58 | 72.83 | 1:00 | 72.83
2001-01-15 | 4:03 | 72.83 | 1:05 | 72.83
2001-01-15 | 4:08 | 72.2 | 1:10 | 72.2
2001-01-15 | 4:13 | 72.2 | 1:15 | 72.2
2001-01-15 | 4:18 | 72.2 | 1:20 | 72.2
2001-01-15 | 4:23 | 72.2 | 1:25 | 72.2
2001-01-15 | 4:28 | 72.2 | 1:30 | 72.2
2001-01-15 | 4:33 | 72.2 | 1:35 | 72.2
2001-01-15 | 4:38 | 72.2 | 1:40 | 72.2
2001-01-15 | 4:43 | 72.2 | 1:45 | 72.2
2001-01-15 | 4:48 | 72.2 | 1:50 | 72.2
2001-01-15 | 4:53 | 72.2 | 1:55 | 72.2
2001-01-15 | 4:58 | 72.2 | 2:00 | 72.2
2001-01-15 | 5:03 | 72.2 | 2:05 | 72.2
2001-01-15 | 5:08 | 72.2 | 2:10 | 72.2
2001-01-15 | 5:13 | 72.2 | 2:15 | 72.2
2001-01-15 | 5:18 | 72.2 | 2:20 | 72.2
2001-01-15 | 5:23 | 71.57 | 2:25 | 71.57
2001-01-15 | 5:28 | 70.95 | 2:30 | 70.95
2001-01-15 | 5:33 | 70.95 | 2:35 | 70.95
2001-01-15 | 5:38 | 70.95 | 2:40 | 70.95
2001-01-15 | 5:43 | 71.57 | 2:45 | 71.57
2001-01-15 | 5:48 | 71.57 | 2:50 | 71.57
2001-01-15 | 5:53 | 71.57 | 2:55 | 71.57
2001-01-15 | 5:58 | 71.57 | 3:00 | 71.57
2001-01-15 | 6:03 | 71.57 | 3:05 | 71.57
2001-01-15 | 6:08 | 71.57 | 3:10 | 71.57
2001-01-15 | 6:13 | 72.2 | 3:15 | 72.2
2001-01-15 | 6:18 | 72.2 | 3:20 | 72.2
2001-01-15 | 6:23 | 72.2 | 3:25 | 72.2
2001-01-15 | 6:28 | 72.2 | 3:30 | 72.2
2001-01-15 | 6:33 | 72.2 | 3:35 | 72.2
2001-01-15 | 6:38 | 72.2 | 3:40 | 72.2
2001-01-15 | 6:43 | 72.2 | 3:45 | 72.2
2001-01-15 | 6:48 | 72.83 | 3:50 | 72.83
2001-01-15 | 6:53 | 72.83 | 3:55 | 72.83
2001-01-15 | 6:58 | 72.83 | 4:00 | 72.83
2001-01-15 | 7:03 | 72.83 | 4:05 | 72.83
2001-01-15 | 7:08 | 72.83 | 4:10 | 72.83
2001-01-15 | 7:13 | 72.83 | 4:15 | 72.83
2001-01-15 | 7:18 | 72.83 | 4:20 | 72.83
2001-01-15 | 7:23 | 72.83 | 4:25 | 72.83
2001-01-15 | 7:28 | 72.83 | 4:30 | 72.83
2001-01-15 | 7:33 | 72.83 | 4:35 | 72.83
2001-01-15 | 7:38 | 72.83 | 4:40 | 72.83
2001-01-15 | 7:43 | 72.83 | 4:45 | 72.83
2001-01-15 | 7:48 | 72.83 | 4:50 | 72.83
2001-01-15 | 7:53 | 72.83 | 4:55 | 72.83
2001-01-15 | 7:58 | 72.83 | 5:00 | 72.83
2001-01-15 | 8:03 | 72.83 | 5:05 | 72.83
2001-01-15 | 8:08 | 72.83 | 5:10 | 72.83
2001-01-15 | 8:13 | 72.2 | 5:15 | 72.2
2001-01-15 | 8:18 | 72.2 | 5:20 | 72.2
2001-01-15 | 8:23 | 72.2 | 5:25 | 72.2
2001-01-15 | 8:28 | 72.2 | 5:30 | 72.2
2001-01-15 | 8:33 | 72.2 | 5:35 | 72.2
2001-01-15 | 8:38 | 72.2 | 5:40 | 72.2
2001-01-15 | 8:43 | 72.2 | 5:45 | 72.2
2001-01-15 | 8:48 | 72.2 | 5:50 | 72.2
2001-01-15 | 8:53 | 72.2 | 5:55 | 72.2
2001-01-15 | 8:58 | 72.2 | 6:00 | 72.2
2001-01-15 | 9:03 | 72.2 | 6:05 | 72.2
2001-01-15 | 9:08 | 72.2 | 6:10 | 72.2
2001-01-15 | 9:13 | 75.39 | 6:15 | 75.39
2001-01-15 | 9:18 | 99.59 | 6:20 | 99.59
2001-01-15 | 9:23 | 103.27 | 6:25 | 103.27
2001-01-15 | 9:28 | 91.84 | 6:30 | 91.84
2001-01-15 | 9:33 | 85.77 | 6:35 | 85.77
2001-01-15 | 9:38 | 69.7 | 6:40 | 69.7
2001-01-15 | 9:43 | 70.95 | 6:45 | 70.95
2001-01-15 | 9:48 | 71.57 | 6:50 | 71.57
2001-01-15 | 9:53 | 71.57 | 6:55 | 71.57
2001-01-15 | 9:58 | 72.2 | 7:00 | 72.2
2001-01-15 | 10:03 | 72.2 | 7:05 | 72.2
2001-01-15 | 10:08 | 72.2 | 7:10 | 72.2
2001-01-15 | 10:13 | 72.2 | 7:15 | 72.2
2001-01-15 | 10:18 | 72.2 | 7:20 | 72.2
2001-01-15 | 10:23 | 91.84 | 7:25 | 91.84
2001-01-15 | 10:28 | 101.79 | 7:30 | 101.79
2001-01-15 | 10:33 | 89.12 | 7:35 | 89.12
2001-01-15 | 10:38 | 83.79 | 7:40 | 83.79
2001-01-15 | 10:43 | 73.47 | 7:45 | 73.47
2001-01-15 | 10:48 | 101.05 | 7:50 | 101.05
2001-01-15 | 10:53 | 102.53 | 7:55 | 102.53
2001-01-15 | 10:58 | 85.1 | 8:00 | 85.1
2001-01-15 | 11:03 | 79.9 | 8:05 | 79.9
2001-01-15 | 11:08 | 83.79 | 8:10 | 83.79
2001-01-15 | 11:13 | 70.32 | 8:15 | 70.32
2001-01-15 | 11:18 | 72.83 | 8:20 | 72.83
2001-01-15 | 11:23 | 72.83 | 8:25 | 72.83
2001-01-15 | 11:28 | 72.83 | 8:30 | 72.83
2001-01-15 | 11:33 | 72.83 | 8:35 | 72.83
2001-01-15 | 11:38 | 72.83 | 8:40 | 72.83
2001-01-15 | 11:43 | 77.97 | 8:45 | 77.97
2001-01-15 | 11:48 | 101.05 | 8:50 | 101.05
2001-01-15 | 11:53 | 107.08 | 8:55 | 107.08
2001-01-15 | 11:58 | 93.22 | 9:00 | 93.22
2001-01-15 | 12:03 | 89.79 | 9:05 | 89.79
9:10
9:15
9:20
9:25
9:30
9:35
9:40
9:45
9:50
9:55
10:00
10:05

## Exhaust Tube Data
Date Time | Temperature (*F) |  | Date Time | Temperature (oF)
2001-01-15 10:08 | 65.93 | 2001-01-15 00:07 | 12:01 | 124.92 | 126.6917
2001-01-15 10:13 | 69.7 | 2001-01-15 00:07 | 12:06 | 128.4633 | 128.8733
2001-01-15 10:18 | 101.05 | 2001-01-15 00:07 | 12:11 | 133.2367 | 132.9189
2001-01-15 10:23 | 142.66 | 2001-01-15 00:07 | 12:16 | 137.0567 | 132.18
2001-01-15 10:28 | 141.49 | 2001-01-15 00:07 | 12:21 | 126.2467 | 126.28
2001-01-15 10:33 | 104.02 | 2001-01-15 00:07 | 12:26 | 115.5367 | 115.9767
2001-01-15 10:38 | 103.27 | 2001-01-15 00:07 | 12:31 | 106.1467 | 110.74
2001-01-15 10:43 | 105.54 | 2001-01-15 00:07 | 12:36 | 110.5367 | 110.35
2001-01-15 10:48 | 108.65 | 2001-01-15 00:07 | 12:41 | 114.3667 | 114.4233
2001-01-15 10:53 | 110.24 | 2001-01-15 00:07 | 12:46 | 118.3667 | 118.5111
2001-01-15 10:58 | 122.12 | 2001-01-15 00:07 | 12:51 | 122.8 | 123.13
2001-01-15 11:03 | 115.99 | 2001-01-15 00:07 | 12:56 | 128.2233 | 127.61
2001-01-15 11:08 | 101.79 | 2001-01-15 00:07 | 13:01 | 131.8067 | 128.6844
2001-01-15 11:13 | 89.79 | 2001-01-15 00:07 | 13:06 | 126.0233 | 125.3967
2001-01-15 11:18 | 97.44 | 2001-01-15 00:07 | 13:11 | 118.36 | 118.2089
2001-01-15 11:23 | 106.31 | 2001-01-15 00:07 | 13:16 | 110.2433 | 112.8611
2001-01-15 11:28 | 114.32 | 2001-01-15 00:07 | 13:21 | 109.98 | 109.9778
2001-01-15 11:33 | 124.89 | 2001-01-15 00:07 | 13:26 | 109.71 | 111.7278
2001-01-15 11:38 | 139.21 | 2001-01-15 00:07 | 13:31 | 115.4933 | 115.9056
2001-01-15 11:43 | 139.21 | 2001-01-15 00:07 | 13:36 | 122.5133 | 123.1789
2001-01-15 11:48 | 133.79 | 2001-01-15 00:07 | 13:41 | 131.53 | 129.4189
2001-01-15 11:53 | 132.75 | 2001-01-15 00:07 | 13:46 | 134.2133 | 132.8889
2001-01-15 11:58 | 125.84 | 2001-01-15 00:07 | 13:51 | 132.9233 | 129.6522
2001-01-15 12:03 | 122.12 | 2001-01-15 00:07 | 13:56 | 121.82 | 121.2078
2001-01-15 12:08 | 124.89 | 2001-01-15 00:07 | 14:01 | 108.88 | 108.9633
2001-01-15 12:13 | 127.75 | 2001-01-15 00:07 | 14:06 | 96.19 | 99.4467
2001-01-15 12:18 | 132.75 | 2001-01-15 00:07 | 14:11 | 93.27 | 95.1322
2001-01-15 12:23 | 139.21 | 2001-01-15 00:07 | 14:16 | 95.9367 | 97.4556
2001-01-15 12:28 | 139.21 | 2001-01-15 00:07 | 14:21 | 103.16 | 102.6933
2001-01-15 12:33 | 100.32 | 2001-01-15 00:07 | 14:26 | 108.9833 | 108.5622
2001-01-15 12:38 | 107.08 | 2001-01-15 00:07 | 14:31 | 113.5433 | 113.0378
2001-01-15 12:43 | 111.04 | 2001-01-15 00:07 | 14:36 | 116.5867 | 116.7356
2001-01-15 12:48 | 113.49 | 2001-01-15 00:07 | 14:41 | 120.0767 | 120.3589
2001-01-15 12:53 | 118.57 | 2001-01-15 00:07 | 14:46 | 124.4133 | 125.1367
2001-01-15 12:58 | 123.04 | 2001-01-15 00:07 | 14:51 | 130.92 | 130.6989
2001-01-15 13:03 | 126.79 | 2001-01-15 00:07 | 14:56 | 136.7633 | 134.38
2001-01-15 13:08 | 134.84 | 2001-01-15 00:07 | 15:01 | 135.4567 | 134.22
2001-01-15 13:13 | 133.79 | 2001-01-15 00:07 | 15:06 | 130.44 | 130.6944
2001-01-15 13:18 | 109.44 | 2001-01-15 00:07 | 15:11 | 126.1867 | 128.04
2001-01-15 13:23 | 111.85 | 2001-01-15 00:07 | 15:16 | 127.4933 | 128.0222
2001-01-15 13:28 | 109.44 | 2001-01-15 00:07 | 15:21 | 130.3867 | 128.4889
2001-01-15 13:33 | 108.65 | 2001-01-15 00:07 | 15:26 | 127.5867 | 128.0844
2001-01-15 13:38 | 111.04 | 2001-01-15 00:07 | 15:31 | 126.28 | 124.24
2001-01-15 13:43 | 126.79 | 2001-01-15 00:07 | 15:36 | 118.8533 | 119.9433
2001-01-15 13:48 | 129.71 | 2001-01-15 00:07 | 15:41 | 114.6967 | 114.6044
2001-01-15 13:53 | 138.09 | 2001-01-15 00:07 | 15:46 | 110.2633 | 112.1911
2001-01-15 13:58 | 134.84 | 2001-01-15 00:07 | 15:51 | 111.6133 | 112.9522
2001-01-15 14:03 | 125.84 | 2001-01-15 00:07 | 15:56 | 116.98 | 117.5633
2001-01-15 14:08 | 104.78 | 2001-01-15 00:07 | 16:01 | 124.0967 | 124.0967
2001-01-15 14:13 | 96.02 | 2001-01-15 00:07 | 16:06 | 131.2133 | 129.48
2001-01-15 14:18 | 87.77 | 2001-01-15 00:07 | 16:11 | 133.13 | 132.1444
2001-01-15 14:23 | 96.02 | 2001-01-15 00:07 | 16:16 | 132.09 | 132.4367
2001-01-15 14:28 | 104.02 | 2001-01-15 00:07 | 16:21 | 132.09 | 132.7789
2001-01-15 14:33 | 109.44 | 2001-01-15 00:07 | 16:26 | 134.1567 | 131.0811
2001-01-15 14:38 | 113.49 | 2001-01-15 00:07 | 16:31 | 126.9967 | 127.1033
2001-01-15 14:43 | 117.7 | 2001-01-15 00:07 | 16:36 | 120.1567 | 119.7633
2001-01-15 14:48 | 118.57 | 2001-01-15 00:07 | 16:41 | 112.1367 | 115.2633
2001-01-15 14:53 | 123.96 | 2001-01-15 00:07 | 16:46 | 113.4967 | 112.6789
2001-01-15 14:58 | 130.71 | 2001-01-15 00:07 | 16:51 | 112.4033 | 112.5889
2001-01-15 15:03 | 138.09 | 2001-01-15 00:07 | 16:56 | 111.8667 | 111.9533
2001-01-15 15:08 | 141.49 | 2001-01-15 00:07 | 17:01 | 111.59 | 112.4222
2001-01-15 15:13 | 126.79 | 2001-01-15 00:07 | 17:06 | 113.81 | 114.6978
2001-01-15 15:18 | 123.04 | 2001-01-15 00:07 | 17:11 | 118.6933 | 120.0489
2001-01-15 15:23 | 128.73 | 2001-01-15 00:07 | 17:16 | 127.6433 | 126.5644
2001-01-15 15:28 | 130.71 | 2001-01-15 00:07 | 17:21 | 133.3567 | 133.2967
2001-01-15 15:33 | 131.72 | 2001-01-15 00:07 | 17:26 | 138.89 | 136.7956
2001-01-15 15:38 | 120.33 | 2001-01-15 00:07 | 17:31 | 138.14 | 135.9267
2001-01-15 15:43 | 126.79 | 2001-01-15 00:07 | 17:36 | 130.75 | 129.4767
2001-01-15 15:48 | 109.44 | 2001-01-15 00:07 | 17:41 | 119.54 | 119.66
2001-01-15 15:53 | 107.86 | 2001-01-15 00:07 | 17:46 | 108.69 | 111.9478
2001-01-15 15:58 | 113.49 | 2001-01-15 00:07 | 17:51 | 107.6133 | 108.5978
2001-01-15 16:03 | 113.49 | 2001-01-15 00:07 | 17:56 | 109.49 | 109.9322
2001-01-15 16:08 | 123.96 | 2001-01-15 00:07 | 18:01 | 112.6933 | 112.3533
2001-01-15 16:13 | 134.84 | 2001-01-15 00:07 | 18:06 | 114.8767 | 114.6167
2001-01-15 16:18 | 134.84 | 2001-01-15 00:07 | 18:11 | 116.28 | 116.8944
2001-01-15 16:23 | 129.71 | 2001-01-15 00:07 | 18:16 | 119.5267 | 118.9267
2001-01-15 16:28 | 131.72 | 2001-01-15 00:07 | 18:21 | 120.9733 | 121.3956
2001-01-15 16:33 | 134.84 | 2001-01-15 00:07 | 18:26 | 123.6867 | 123.6556
2001-01-15 16:38 | 135.91 | 2001-01-15 00:07 | 18:31 | 126.3067 | 127.5311
2001-01-15 16:43 | 110.24 | 2001-01-15 00:07 | 18:36 | 132.6 | 132.2411
2001-01-15 16:48 | 114.32 | 2001-01-15 00:07 | 18:41 | 137.8167 | 136.1933
2001-01-15 16:53 | 111.85 | 2001-01-15 00:07 | 18:46 | 138.1633 | 138.0478
2001-01-15 16:58 | 114.32 | 2001-01-15 00:07 | 18:51 | 138.1633 | 136.9656
2001-01-15 17:03 | 111.04 | 2001-01-15 00:07 | 18:56 | 134.57 | 134.99
2001-01-15 17:08 | 110.24 | 2001-01-15 00:07 | 19:01 | 132.2367 | 131.32
2001-01-15 17:13 | 113.49 | 2001-01-15 00:07 | 19:06 | 127.1533 | 128.2011
2001-01-15 17:18 | 117.7 | 2001-01-15 00:07 | 19:11 | 125.2133 | 124.9467
2001-01-15 17:23 | 124.89 | 2001-01-15 00:07 | 19:16 | 122.4733 | 122.6911
2001-01-15 17:28 | 140.34 | 2001-01-15 00:07 | 19:21 | 120.3867 | 119.9078
2001-01-15 17:33 | 134.84 | 2001-01-15 00:07 | 19:26 | 116.8633 | 117.6578
2001-01-15 17:38 | 141.49 | 2001-01-15 00:07 | 19:31 | 115.7233 | 116.1033
2001-01-15 17:43 | 138.09 | 2001-01-15 00:07 | 19:36 | 115.7233 | 116.0989
2001-01-15 17:48 | 112.67 | 2001-01-15 00:07 | 19:41 | 116.85 | 117.6622
2001-01-15 17:53 | 107.86 | 2001-01-15 00:07 | 19:46 | 120.4133 | 121.9989
2001-01-15 17:58 | 105.54 | 2001-01-15 00:07 | 19:51 | 128.7333 | 128.8656
2001-01-15 18:03 | 109.44 | 2001-01-15 00:07 | 19:56 | 137.45 | 133.2644
2001-01-15 18:08 | 113.49 | 2001-01-15 00:07 | 20:01 | 133.61 | 131.4667
2001-01-15 18:13 | 115.15 | 2001-01-15 00:07 | 20:06 | 123.34 | 123.2989
2001-01-15 18:18 | 115.99 | 2001-01-15 00:07 | 20:11 | 112.9467 | 116.2278
2001-01-15 18:23 | 117.7 | 2001-01-15 00:07 | 20:16 | 112.3967 | 112.8544
2001-01-15 18:28 | 124.89 | 2001-01-15 00:07 | 20:21 | 113.22 | 113.4089
2001-01-15 18:33 | 120.33 | 2001-01-15 00:07 | 20:26 | 114.61 | 114.7056
2001-01-15 18:38 | 125.84 | 2001-01-15 00:07 | 20:31 | 116.2867 | 116.6967
2001-01-15 18:43 | 132.75 | 2001-01-15 00:07 | 20:36 | 119.1933 | 120.4633
2001-01-15 18:48 | 139.21 | 2001-01-15 00:07 | 20:41 | 125.91 | 125.4589
2001-01-15 18:53 | 141.49 | 2001-01-15 00:07 | 20:46 | 131.2733 | 130.5644
2001-01-15 18:58 | 133.79 | 2001-01-15 00:07 | 20:51 | 134.51 | 133.0756
2001-01-15 19:03 | 139.21 | 2001-01-15 00:07 | 20:56 | 133.4433 | 133.6833
2001-01-15 19:08 | 130.71 | 2001-01-15 00:07 | 21:01 | 133.0967 | 130.6222
2001-01-15 19:13 | 126.79 | 2001-01-15 00:07 | 21:06 | 125.3267 | 124.5256
2001-01-15 19:18 | 123.96 | 2001-01-15 00:07 | 21:11 | 115.1533 | 115.8667
2001-01-15 19:23 | 124.89 | 2001-01-15 00:07 | 21:16 | 107.12 | 109.7978
2001-01-15 19:28 | 118.57 | 2001-01-15 00:07 | 21:21 | 107.12 | 107.9833
2001-01-15 19:33 | 117.7 | 2001-01-15 00:07 | 21:26 | 109.71 | 109.2022
2001-01-15 19:38 | 114.32 | 2001-01-15 00:07 | 21:31 | 110.7767 | 111.4356
2001-01-15 19:43 | 115.15 | 2001-01-15 00:07 | 21:36 | 113.82 | 112.8056
2001-01-15 19:48 | 117.7 | 2001-01-15 00:07 | 21:41 | 113.82 | 114.47
2001-01-15 19:53 | 117.7 | 2001-01-15 00:07 | 21:46 | 115.77 | 115.3156
2001-01-15 19:58 | 125.84 | 2001-01-15 00:07 | 21:51 | 116.3567 | 117.4944
2001-01-15 20:03 | 142.66 | 2001-01-15 00:07 | 21:56 | 120.3567 | 120.2489
2001-01-15 20:08 | 143.85 | 2001-01-15 00:07 | 22:01 | 124.0333 | 124.1878
2001-01-15 20:13 | 114.32 | 2001-01-15 00:07 | 22:06 | 128.1733 | 125.7322
2001-01-15 20:18 | 111.85 | 2001-01-15 00:07 | 22:11 | 124.99 | 124.0856
2001-01-15 20:23 | 112.67 | 2001-01-15 00:07 | 22:16 | 119.0933 | 118.6467
2001-01-15 20:28 | 112.67 | 2001-01-15 00:07 | 22:21 | 111.8567 | 114.1778
2001-01-15 20:33 | 114.32 | 2001-01-15 00:07 | 22:26 | 111.5833 | 112.7067
2001-01-15 20:38 | 116.84 | 2001-01-15 00:07 | 22:31 | 114.68 | 114.7789
2001-01-15 20:43 | 117.7 | 2001-01-15 00:07 | 22:36 | 118.0733 | 117.3111
2001-01-15 20:48 | 123.04 | 2001-01-15 00:07 | 22:41 | 119.18 | 118.91
2001-01-15 20:53 | 136.99 | 2001-01-15 00:07 | 22:46 | 119.4767 | 118.7033
2001-01-15 20:58 | 133.79 | 2001-01-15 00:07 | 22:51 | 117.4533 | 116.9667
2001-01-15 21:03 | 132.75 | 2001-01-15 00:07 | 22:56 | 113.97 | 112.8089
2001-01-15 21:08 | 133.79 | 2001-01-15 00:07 | 23:01 | 107.0033 | 108.78
2001-01-15 21:13 | 132.75 | 2001-01-15 00:07 | 23:06 | 105.3667 | 108.1678
2001-01-15 21:18 | 109.44 | 2001-01-15 00:07 | 23:11 | 112.1333 | 114.0744
2001-01-15 21:23 | 103.27 | 2001-01-15 00:07 | 23:16 | 124.7233 | 123.0278
2001-01-15 21:28 | 108.65 | 2001-01-15 00:07 | 23:21 | 132.2267 | 130.6089
2001-01-15 21:33 | 109.44 | 2001-01-15 00:07 | 23:26 | 134.8767 | 133.2856
2001-01-15 21:38 | 111.04 | 2001-01-15 00:07 | 23:31 | 132.7533 | 133.1233
2001-01-15 21:43 | 111.85 | 2001-01-15 00:07 | 23:36 | 131.74 | 131.9622
2001-01-15 21:48 | 118.57 | 2001-01-15 00:07 | 23:41 | 131.3933 | 130.9611
2001-01-15 21:53 | 111.04 | 2001-01-15 00:07 | 23:46 | 129.75 | 130.6356
2001-01-15 21:58 | 117.7 | 2001-01-15 00:07 | 23:51 | 130.7633 | 128.6578
2001-01-15 22:03 | 120.33 | 2001-01-15 00:07 | 23:56 | 125.46 | 125.8422
2001-01-15 22:08 | 123.04 | 2001-01-15 00:07 | 24:01 | 121.3033 | 121.61
2001-01-15 22:13 | 128.73 | 2001-01-15 00:07 | 24:06 | 118.0667 | 120.9133
2001-01-15 22:18 | 132.75 | 2001-01-15 00:07 | 24:11 | 123.37 | 123.7656
2001-01-15 22:23 | 113.49 | 2001-01-15 00:07 | 24:16 | 129.86 | 129.0078
2001-01-15 22:28 | 111.04 | 2001-01-15 00:07 | 24:21 | 133.7933 | 131.6089
2001-01-15 22:33 | 111.04 | 2001-01-15 00:07 | 24:26 | 131.1733 | 131.8167
2001-01-15 22:38 | 112.67 | 2001-01-15 00:07 | 24:31 | 130.4833 | 131.1989
2001-01-15 22:43 | 120.33 | 2001-01-15 00:07 | 24:36 | 131.94 | 133.0456
2001-01-15 22:48 | 121.22 | 2001-01-15 00:07 | 24:41 | 136.7133 | 135.3522
2001-01-15 22:53 | 115.99 | 2001-01-15 00:07 | 24:46 | 137.4033 | 136.9267
2001-01-15 22:58 | 121.22 | 2001-01-15 00:07 | 24:51 | 136.6633 | 136.6633
2001-01-15 23:03 | 115.15 | 2001-01-15 00:07 | 24:56 | 135.9233 | 135.8278
2001-01-15 23:08 | 105.54 | 2001-01-15 00:07 | 25:01 | 134.8967 | 133.6889
2001-01-15 23:13 | 100.32 | 2001-01-15 00:07 | 25:06 | 130.2467 | 130.9878
2001-01-15 23:18 | 110.24 | 2001-01-15 00:07 | 25:11 | 127.82 | 129.0878
2001-01-15 23:23 | 125.84 | 2001-01-15 00:07 | 25:16 | 129.1967 | 129.9322
2001-01-15 23:28 | 138.09 | 2001-01-15 00:07 | 25:21 | 132.78 | 132.0389
2001-01-15 23:33 | 132.75 | 2001-01-15 00:07 | 25:26 | 134.14 | 133.57
2001-01-15 23:38 | 133.79 | 2001-01-15 00:07 | 25:31 | 133.79 | 133.9067
2001-01-15 23:43 | 131.72 | 2001-01-15 00:07 | 25:36 | 133.79 | 133.3367
2001-01-15 23:48 | 129.71 | 2001-01-15 00:07 | 25:41 | 132.43 | 129.3278
2001-01-15 23:53 | 132.75 | 2001-01-15 00:07 | 25:46 | 121.7633 | 120.8111
2001-01-15 23:58 | 126.79 | 2001-01-15 00:07 | 25:51 | 108.24 | 108.3122
2001-01-16 00:03 | 132.75 | 2001-01-15 00:07 | 25:56 | 94.9333 | 97.8111
2001-01-16 00:08 | 116.84 | 2001-01-15 00:07 | 26:01 | 90.26 | 91.0633
2001-01-16 00:13 | 114.32 | 2001-01-15 00:07 | 26:06 | 87.9967 | 88.23
2001-01-16 00:18 | 123.04 | 2001-01-15 00:07 | 26:11 | 86.4333 | 86.5122
2001-01-16 00:23 | 132.75 | 2001-01-15 00:07 | 26:16 | 85.1067 | 85.1822
2001-01-16 00:28 | 133.79 | 2001-01-15 00:07 | 26:21 | 84.0067 | 83.9389
2001-01-16 00:33 | 134.84 | 2001-01-15 00:07 | 26:26 | 82.7033 | 82.5622
2001-01-16 00:38 | 124.89 | 2001-01-15 00:07 | 26:31 | 80.9767 | 80.9067
2001-01-16 00:43 | 131.72 | 2001-01-15 00:07 | 26:36 | 79.04 | 79.1844
2001-01-16 00:48 | 139.21 | 2001-01-15 00:07 | 26:41 | 77.5367 | 77.7511
2001-01-16 00:53 | 139.21 | 2001-01-15 00:07 | 26:46 | 76.6767 | 76.82
2001-01-16 00:58 | 133.79 | 2001-01-15 00:07 | 26:51 | 76.2467 | 76.3178
2001-01-16 01:03 | 136.99 | 2001-01-15 00:07 | 26:56 | 76.03 | 76.1022
2001-01-16 01:08 | 136.99 | 2001-01-15 00:07 | 27:01 | 76.03 | 75.9589
2001-01-16 01:13 | 130.71 | 2001-01-15 00:07 | 27:06 | 75.8167 | 75.8167
2001-01-16 01:18 | 123.04 | 2001-01-15 00:07 | 27:11 | 75.6033 | 75.6033
2001-01-16 01:23 | 129.71 | 2001-01-15 00:07 | 27:16 | 75.39 | 75.4611
2001-01-16 01:28 | 134.84 | 2001-01-15 00:07 | 27:21 | 75.39 | 75.3178
2001-01-16 01:33 | 133.79 | 2001-01-15 00:07 | 27:26 | 75.1733 | 75.1022
2001-01-16 01:38 | 133.79 | 2001-01-15 00:07 | 27:31 | 74.7433 | 74.7433
2001-01-16 01:43 | 133.79 | 2001-01-15 00:07 | 27:36 | 74.3133 | 74.3856
2001-01-16 01:48 | 133.79 | 2001-01-15 00:07 | 27:41 | 74.1 | 74.1711
2001-01-16 01:53 | 129.71 | 2001-01-15 00:07 | 27:46 | 74.1 | 74.1
2001-01-16 01:58 | 101.79 | 2001-01-15 00:07 | 27:51 | 74.1 | 74.1
2001-01-16 02:03 | 93.22 | 2001-01-15 00:07 | 27:56 | 74.1 | 74.03
2001-01-16 02:08 | 89.79 | 2001-01-15 00:07 | 28:01 | 73.89 | 73.89
2001-01-16 02:13 | 87.77 | 2001-01-15 00:07 | 28:06 | 73.68 | 73.68
2001-01-16 02:18 | 86.43 | 2001-01-15 00:07 | 28:11 | 73.47 | 73.54
2001-01-16 02:23 | 85.1 | 2001-01-15 00:07 | 28:16 | 73.47 | 73.3989
2001-01-16 02:28 | 83.79 | 2001-01-15 00:07 | 28:21 | 73.2567 | 73.3278
2001-01-16 02:33 | 83.13 | 2001-01-15 00:07 | 28:26 | 73.2567 | 73.1856
2001-01-16 02:38 | 81.19 | 2001-01-15 00:07 | 28:31 | 73.0433 | 73.1856
2001-01-16 02:43 | 78.61 | 2001-01-15 00:07 | 28:36 | 73.2567 | 73.1856
2001-01-16 02:48 | 77.32 | 2001-01-15 00:07 | 28:41 | 73.2567 | 73.3278
2001-01-16 02:53 | 76.68 | 2001-01-15 00:07 | 28:46 | 73.47 | 73.3989
2001-01-16 02:58 | 76.03 | 2001-01-15 00:07 | 28:51 | 73.47 | 73.3989
2001-01-16 03:03 | 76.03 | 2001-01-15 00:07 | 28:56 | 73.2567 | 73.2567
2001-01-16 03:08 | 76.03 | 2001-01-15 00:07 | 29:01 | 73.0433 | 73.0433
2001-01-16 03:13 | 76.03 | 2001-01-15 00:07 | 29:06 | 72.83 | 72.9011
2001-01-16 03:18 | 75.39 | 2001-01-15 00:07 | 29:11 | 72.83 | 72.83
2001-01-16 03:23 | 75.39 | 2001-01-15 00:07 | 29:16 | 72.83 | 72.83
2001-01-16 03:28 | 75.39 | 2001-01-15 00:07 | 29:21 | 72.83 | 72.83
2001-01-16 03:33 | 75.39 | 2001-01-15 00:07 | 29:26 | 72.83 | 72.83
2001-01-16 03:38 | 74.74 | 2001-01-15 00:07 | 29:31 | 72.83 | 72.83
2001-01-16 03:43 | 74.1 | 2001-01-15 00:07 | 29:36 | 72.83 | 74.79
2001-01-16 03:48 | 74.1 | 2001-01-15 00:07 | 29:41 | 78.71 | 79.7233
2001-01-16 03:53 | 74.1 | 2001-01-15 00:07 | 29:46 | 87.63 | 88.1222
2001-01-16 03:58 | 74.1 | 2001-01-15 00:07 | 29:51 | 98.0267 | 96.0667
2001-01-16 04:03 | 74.1 | 2001-01-15 00:07 | 29:56 | 102.5433 | 102.1322
2001-01-16 04:08 | 74.1 | 2001-01-15 00:07 | 30:01 | 105.8267 | 106.3489
2001-01-16 04:13 | 73.47 | 2001-01-15 00:07 | 30:06 | 110.6767 | 111.59
2001-01-16 04:18 | 73.47 | 2001-01-15 00:07 | 30:11 | 118.2667 | 118.1
2001-01-16 04:23 | 73.47 | 2001-01-15 00:07 | 30:16 | 125.3567 | 124.3422
2001-01-16 04:28 | 73.47 | 2001-01-15 00:07 | 30:21 | 129.4033 | 128.8322
2001-01-16 04:33 | 72.83 | 2001-01-15 00:07 | 30:26 | 131.7367 | 130.5233
2001-01-16 04:38 | 73.47 | 2001-01-15 00:07 | 30:31 | 130.43 | 127.3278
2001-01-16 04:43 | 72.83 | 2001-01-15 00:07 | 30:36 | 119.8167 | 120.2156
2001-01-16 04:48 | 73.47 | 2001-01-15 00:07 | 30:41 | 110.4 | 111.8789
2001-01-16 04:53 | 73.47 | 2001-01-15 00:07 | 30:46 | 105.42 | 108.8889
2001-01-16 04:58 | 73.47 | 2001-01-15 00:07 | 30:51 | 110.8467 | 110.4856
2001-01-16 05:03 | 73.47 | 2001-01-15 00:07 | 30:56 | 115.19 | 114.9856
2001-01-16 05:08 | 72.83 | 2001-01-15 00:07 | 31:01 | 118.92 | 119.2944
2001-01-16 05:13 | 72.83 | 2001-01-15 00:07 | 31:06 | 123.7733 | 124.0822
2001-01-16 05:18 | 72.83 | 2001-01-15 00:07 | 31:11 | 129.5533 | 129.2989
2001-01-16 05:23 | 72.83 | 2001-01-15 00:07 | 31:16 | 134.57 | 134.0789
2001-01-16 05:28 | 72.83 | 2001-01-15 00:07 | 31:21 | 138.1133 | 135.8133
2001-01-16 05:33 | 72.83 | 2001-01-15 00:07 | 31:26 | 134.7567 | 131.6789
2001-01-16 05:38 | 72.83 | 2001-01-15 00:07 | 31:31 | 122.1667 | 120.9744
2001-01-16 05:43 | 72.83 | 2001-01-15 00:07 | 31:36 | 106 | 107.0844
2001-01-16 05:48 | 72.83 | 2001-01-15 00:07 | 31:41 | 93.0867 | 95.5544
2001-01-16 05:53 | 90.47 | 2001-01-15 00:07 | 31:46 | 87.5767 | 90.6833
2001-01-16 05:58 | 99.59 | 2001-01-15 00:07 | 31:51 | 91.3867 | 93.3267
2001-01-16 06:03 | 104.02 | 2001-01-15 00:07 | 31:56 | 101.0167 | 102.27
2001-01-16 06:08 | 104.02 | 2001-01-15 00:07 | 32:01 | 114.4067 | 113.2189
2001-01-16 06:13 | 109.44 | 2001-01-15 00:07 | 32:06 | 124.2333 | 122.82
2001-01-16 06:18 | 118.57 | 2001-01-15 00:07 | 32:11 | 129.82 | 126.3444
2001-01-16 06:23 | 126.79 | 2001-01-15 00:07 | 32:16 | 124.98 | 125.3122
2001-01-16 06:28 | 130.71 | 2001-01-15 00:07 | 32:21 | 121.1367 | 119.3944
2001-01-16 06:33 | 130.71 | 2001-01-15 00:07 | 32:26 | 112.0667 | 114.6567
2001-01-16 06:38 | 133.79 | 2001-01-15 00:07 | 32:31 | 110.7667 | 109.6289
2001-01-16 06:43 | 126.79 | 2001-01-15 00:07 | 32:36 | 106.0533 | 107.6244
2001-01-16 06:48 | 98.87 | 2001-01-15 00:07 | 32:41 | 106.0533 | 106.1389
2001-01-16 06:53 | 105.54 | 2001-01-15 00:07 | 32:46 | 106.31 | 106.3111
2001-01-16 06:58 | 111.85 | 2001-01-15 00:07 | 32:51 | 106.57 | 107.4589
2001-01-16 07:03 | 115.15 | 2001-01-15 00:07 | 32:56 | 109.4967 | 109.1367
2001-01-16 07:08 | 118.57 | 2001-01-15 00:07 | 33:01 | 111.3433 | 110.8156
2001-01-16 07:13 | 123.04 | 2001-01-15 00:07 | 33:06 | 111.6067 | 111.2444
2001-01-16 07:18 | 129.71 | 2001-01-15 00:07 | 33:11 | 110.7833 | 110.3567
2001-01-16 07:23 | 135.91 | 2001-01-15 00:07 | 33:16 | 108.68 | 107.2856
2001-01-16 07:28 | 138.09 | 2001-01-15 00:07 | 33:21 | 102.3933 | 103.2889
2001-01-16 07:33 | 140.34 | 2001-01-15 00:07 | 33:26 | 98.7933 | 100.8767
2001-01-16 07:38 | 125.84 | 2001-01-15 00:07 | 33:31 | 101.4433 | 104.5656
2001-01-16 07:43 | 100.32 | 2001-01-15 00:07 | 33:36 | 113.46 | 113.4478
2001-01-16 07:48 | 91.84 | 2001-01-15 00:07 | 33:41 | 125.44 | 124.0578
2001-01-16 07:53 | 87.1 | 2001-01-15 00:07 | 33:46 | 133.2733 | 131.43
2001-01-16 07:58 | 83.79 | 2001-01-15 00:07 | 33:51 | 135.5767 | 134.4533
2001-01-16 08:03 | 103.27 | 2001-01-15 00:07 | 33:56 | 134.51 | 130.71
2001-01-16 08:08 | 115.99 | 2001-01-15 00:07 | 34:01 | 122.0433 | 122.3544
2001-01-16 08:13 | 123.96 | 2001-01-15 00:07 | 34:06 | 110.51 | 110.3156
2001-01-16 08:18 | 132.75 | 2001-01-15 00:07 | 34:11 | 98.3933 | 101.8022
2001-01-16 08:23 | 132.75 | 2001-01-15 00:07 | 34:16 | 96.5033 | 96.74
2001-01-16 08:28 | 109.44 | 2001-01-15 00:07 | 34:21 | 95.3233 | 95.5589
2001-01-16 08:33 | 121.22 | 2001-01-15 00:07 | 34:26 | 94.85 | 95.3989
2001-01-16 08:38 | 105.54 | 2001-01-15 00:07 | 34:31 | 96.0233 | 96.8467
2001-01-16 08:43 | 105.54 | 2001-01-15 00:07 | 34:36 | 99.6667 | 100.6711
2001-01-16 08:48 | 107.08 | 2001-01-15 00:07 | 34:41 | 106.3233 | 106.9489
2001-01-16 08:53 | 105.54 | 2001-01-15 00:07 | 34:46 | 114.8567 | 114.8089
2001-01-16 08:58 | 106.31 | 2001-01-15 00:07 | 34:51 | 123.2467 | 121.3356
2001-01-16 09:03 | 107.86 | 2001-01-15 00:07 | 34:56 | 125.9033 | 125.3289
2001-01-16 09:08 | 114.32 | 2001-01-15 00:07 | 35:01 | 126.8367 | 125.2733
2001-01-16 09:13 | 111.85 | 2001-01-15 00:07 | 35:06 | 123.08 | 123.9289
2001-01-16 09:18 | 108.65 | 2001-01-15 00:07 | 35:11 | 121.87 | 121.2733
2001-01-16 09:23 | 111.85 | 2001-01-15 00:07 | 35:16 | 118.87 | 119.4867
2001-01-16 09:28 | 105.54 | 2001-01-15 00:07 | 35:21 | 117.72 | 116.5456
2001-01-16 09:33 | 89.79 | 2001-01-15 00:07 | 35:26 | 113.0467 | 112.9322
2001-01-16 09:38 | 101.05 | 2001-01-15 00:07 | 35:31 | 108.03 | 108.5411
2001-01-16 09:43 | 113.49 | 2001-01-15 00:07 | 35:36 | 104.5467 | 105.88
2001-01-16 09:48 | 125.84 | 2001-01-15 00:07 | 35:41 | 105.0633 | 105.6533
2001-01-16 09:53 | 136.99 | 2001-01-15 00:07 | 35:46 | 107.35 | 106.8456
2001-01-16 09:58 | 136.99 | 2001-01-15 00:07 | 35:51 | 108.1233 | 107.8656
2001-01-16 10:03 | 132.75 | 2001-01-15 00:07 | 35:56 | 108.1233 | 108.0356
2001-01-16 10:08 | 133.79 | 2001-01-15 00:07 | 36:01 | 107.86 | 107.0289
2001-01-16 10:13 | 99.59 | 2001-01-15 00:07 | 36:06 | 105.1033 | 105.0233
2001-01-16 10:18 | 98.15 | 2001-01-15 00:07 | 36:11 | 102.1067 | 102.4311
2001-01-16 10:23 | 97.44 | 2001-01-15 00:07 | 36:16 | 100.0833 | 101.6767
2001-01-16 10:28 | 93.92 | 2001-01-15 00:07 | 36:21 | 102.84 | 103.6378
2001-01-16 10:33 | 94.61 | 2001-01-15 00:07 | 36:26 | 107.99 | 107.1233
2001-01-16 10:38 | 96.02 | 2001-01-15 00:07 | 36:31 | 110.54 | 109.7778
2001-01-16 10:43 | 97.44 | 2001-01-15 00:07 | 36:36 | 110.8033 | 110.1733
2001-01-16 10:48 | 105.54 | 2001-01-15 00:07 | 36:41 | 109.1767 | 109.6311
2001-01-16 10:53 | 115.99 | 2001-01-15 00:07 | 36:46 | 108.9133 | 110.0067
2001-01-16 10:58 | 123.04 | 2001-01-15 00:07 | 36:51 | 111.93 | 111.9389
2001-01-16 11:03 | 130.71 | 2001-01-15 00:07 | 36:56 | 114.9733 | 114.7744
2001-01-16 11:08 | 123.96 | 2001-01-15 00:07 | 37:01 | 117.42 | 116.9956
2001-01-16 11:13 | 125.84 | 2001-01-15 00:07 | 37:06 | 118.5933 | 117.4556
2001-01-16 11:18 | 119.44 | 2001-01-15 00:07 | 37:11 | 116.3533 | 117.4833
2001-01-16 11:23 | 120.33 | 2001-01-15 00:07 | 37:16 | 117.5033 | 117.3222
2001-01-16 11:28 | 116.84 | 2001-01-15 00:07 | 37:21 | 118.11 | 119.5678
2001-01-16 11:33 | 115.99 | 2001-01-15 00:07 | 37:26 | 123.09 | 122.6822
2001-01-16 11:38 | 106.31 | 2001-01-15 00:07 | 37:31 | 126.8467 | 126.6733
2001-01-16 11:43 | 101.79 | 2001-01-15 00:07 | 37:36 | 130.0833 | 129.8989
2001-01-16 11:48 | 105.54 | 2001-01-15 00:07 | 37:41 | 132.7667 | 132.57
2001-01-16 11:53 | 107.86 | 2001-01-15 00:07 | 37:46 | 134.86 | 134.7556
2001-01-16 11:58 | 108.65 | 2001-01-15 00:07 | 37:51 | 136.64 | 135.8144
2001-01-16 12:03 | 107.86 | 2001-01-15 00:07 | 37:56 | 135.9433 | 132.6811
2001-01-16 12:08 | 107.86 | 2001-01-15 00:07 | 38:01 | 125.46 | 124.2011
2001-01-16 12:13 | 107.86 | 2001-01-15 00:07 | 38:06 | 111.2 | 111.18
2001-01-16 12:18 | 99.59 | 2001-01-15 00:07 | 38:11 | 96.88 | 99.53
2001-01-16 12:23 | 98.87 | 2001-01-15 00:07 | 38:16 | 90.51 | 91.28
2001-01-16 12:28 | 101.79 | 2001-01-15 00:07 | 38:21 | 86.45 | 86.9189
2001-01-16 12:33 | 107.86 | 2001-01-15 00:07 | 38:26 | 83.7967 | 84.0267
2001-01-16 12:38 | 114.32 | 2001-01-15 00:07 | 38:31 | 81.8333 | 83.6089
2001-01-16 12:43 | 109.44 | 2001-01-15 00:07 | 38:36 | 85.1967 | 86.7956
2001-01-16 12:48 | 108.65 | 2001-01-15 00:07 | 38:41 | 93.3567 | 94.39
2001-01-16 12:53 | 109.44 | 2001-01-15 00:07 | 38:46 | 104.6167 | 103.68
2001-01-16 12:58 | 108.65 | 2001-01-15 00:07 | 38:51 | 113.0667 | 111.9067
2001-01-16 13:03 | 117.7 | 2001-01-15 00:07 | 38:56 | 118.0367 | 117.4511
2001-01-16 13:08 | 118.57 | 2001-01-15 00:07 | 39:01 | 121.25 | 121.0922
2001-01-16 13:13 | 115.99 | 2001-01-15 00:07 | 39:06 | 123.99 | 123.8022
2001-01-16 13:18 | 121.22 | 2001-01-15 00:07 | 39:11 | 126.1667 | 126.1911
2001-01-16 13:23 | 111.85 | 2001-01-15 00:07 | 39:16 | 128.4167 | 126.4667
2001-01-16 13:28 | 119.44 | 2001-01-15 00:07 | 39:21 | 124.8167 | 123.4644
2001-01-16 13:33 | 123.04 | 2001-01-15 00:07 | 39:26 | 117.16 | 117.4378
2001-01-16 13:38 | 126.79 | 2001-01-15 00:07 | 39:31 | 110.3367 | 112.3333
2001-01-16 13:43 | 130.71 | 2001-01-15 00:07 | 39:36 | 109.5033 | 111.0267
2001-01-16 13:48 | 132.75 | 2001-01-15 00:07 | 39:41 | 113.24 | 112.92
2001-01-16 13:53 | 134.84 | 2001-01-15 00:07 | 39:46 | 116.0167 | 115.95
2001-01-16 13:58 | 136.99 | 2001-01-15 00:07 | 39:51 | 118.5933 | 119.15
2001-01-16 14:03 | 138.09 | 2001-01-15 00:07 | 39:56 | 122.84 | 123
2001-01-16 14:08 | 132.75 | 2001-01-15 00:07 | 40:01 | 127.5667 | 127.8656
2001-01-16 14:13 | 105.54 | 2001-01-15 00:07 | 40:06 | 133.19 | 132.48
2001-01-16 14:18 | 95.31 | 2001-01-15 00:07 | 40:11 | 136.6833 | 134.6456
2001-01-16 14:23 | 89.79 | 2001-01-15 00:07 | 40:16 | 134.0633 | 133.1622
2001-01-16 14:28 | 86.43 | 2001-01-15 00:07 | 40:21 | 128.74 | 128.1244
2001-01-16 14:33 | 83.13 | 2001-01-15 00:07 | 40:26 | 121.57 | 123.3544
2001-01-16 14:38 | 81.83 | 2001-01-15 00:07 | 40:31 | 119.7533 | 120.3589
2001-01-16 14:43 | 80.54 | 2001-01-15 00:07 | 40:36 | 119.7533 | 120.87
2001-01-16 14:48 | 93.22 | 2001-01-15 00:07 | 40:41 | 123.1033 | 123.3511
2001-01-16 14:53 | 106.31 | 2001-01-15 00:07 | 40:46 | 127.1967 | 126.5667
2001-01-16 14:58 | 114.32 | 2001-01-15 00:07 | 40:51 | 129.4 | 129.3367
2001-01-16 15:03 | 118.57 | 2001-01-15 00:07 | 40:56 | 131.4133 | 131.8278
2001-01-16 15:08 | 121.22 | 2001-01-15 00:07 | 41:01 | 134.67 | 134.0311
2001-01-16 15:13 | 123.96 | 2001-01-15 00:07 | 41:06 | 136.01 | 132.34
2001-01-16 15:18 | 126.79 | 2001-01-15 00:07 | 41:11 | 126.34 | 125.1522
2001-01-16 15:23 | 127.75 | 2001-01-15 00:07 | 41:16 | 113.1067 | 114.9278
2001-01-16 15:28 | 130.71 | 2001-01-15 00:07 | 41:21 | 105.3367 | 109.2667
2001-01-16 15:33 | 115.99 | 2001-01-15 00:07 | 41:26 | 109.3567 | 110.0767
2001-01-16 15:38 | 104.78 | 2001-01-15 00:07 | 41:31 | 115.5367 | 115.1933
2001-01-16 15:43 | 110.24 | 2001-01-15 00:07 | 41:36 | 120.6867 | 120.5111
2001-01-16 15:48 | 113.49 | 2001-01-15 00:07 | 41:41 | 125.31 | 124.9222
2001-01-16 15:53 | 115.99 | 2001-01-15 00:07 | 41:46 | 128.77 | 127.4111
2001-01-16 15:58 | 118.57 | 2001-01-15 00:07 | 41:51 | 128.1533 | 127.7122
2001-01-16 16:03 | 121.22 | 2001-01-15 00:07 | 41:56 | 126.2133 | 126.9722
2001-01-16 16:08 | 128.73 | 2001-01-15 00:07 | 42:01 | 126.55 | 126.0378
2001-01-16 16:13 | 132.75 | 2001-01-15 00:07 | 42:06 | 125.35 | 127.0944
2001-01-16 16:18 | 138.09 | 2001-01-15 00:07 | 42:11 | 129.3833 | 128.7467
2001-01-16 16:23 | 139.21 | 2001-01-15 00:07 | 42:16 | 131.5067 | 132.6289
2001-01-16 16:28 | 124.89 | 2001-01-15 00:07 | 42:21 | 136.9967 | 135.4133
2001-01-16 16:33 | 122.12 | 2001-01-15 00:07 | 42:26 | 137.7367 | 134.9411
2001-01-16 16:38 | 117.7 | 2001-01-15 00:07 | 42:31 | 130.09 | 128.2856
2001-01-16 16:43 | 119.44 | 2001-01-15 00:07 | 42:36 | 117.03 | 117.7278
2001-01-16 16:48 | 122.12 | 2001-01-15 00:07 | 42:41 | 106.0633 | 110.1956
2001-01-16 16:53 | 127.75 | 2001-01-15 00:07 | 42:46 | 107.4933 | 110.3567
2001-01-16 16:58 | 131.72 | 2001-01-15 00:07 | 42:51 | 117.5133 | 117.2267
2001-01-16 17:03 | 128.73 | 2001-01-15 00:07 | 42:56 | 126.6733 | 125.6922
2001-01-16 17:08 | 133.79 | 2001-01-15 00:07 | 43:01 | 132.89 | 132.3233
2001-01-16 17:13 | 141.49 | 2001-01-15 00:07 | 43:06 | 137.4067 | 133.83
2001-01-16 17:18 | 132.75 | 2001-01-15 00:07 | 43:11 | 131.1933 | 127.8233
2001-01-16 17:23 | 104.78 | 2001-01-15 00:07 | 43:16 | 114.87 | 114.9222
2001-01-16 17:28 | 101.79 | 2001-01-15 00:07 | 43:21 | 98.7033 | 101.8878
2001-01-16 17:33 | 109.44 | 2001-01-15 00:07 | 43:26 | 92.09 | 95.2978
2001-01-16 17:38 | 116.84 | 2001-01-15 00:07 | 43:31 | 95.1 | 95.2844
2001-01-16 17:43 | 120.33 | 2001-01-15 00:07 | 43:36 | 98.6633 | 98.4433
2001-01-16 17:48 | 124.89 | 2001-01-15 00:07 | 43:41 | 101.5667 | 101.3356
2001-01-16 17:53 | 130.71 | 2001-01-15 00:07 | 43:46 | 103.7767 | 103.46
2001-01-16 17:58 | 130.71 | 2001-01-15 00:07 | 43:51 | 105.0367 | 105.1311
2001-01-16 18:03 | 123.04 | 2001-01-15 00:07 | 43:56 | 106.58 | 106.9422
2001-01-16 18:08 | 124.89 | 2001-01-15 00:07 | 44:01 | 109.21 | 109.5989
2001-01-16 18:13 | 131.72 | 2001-01-15 00:07 | 44:06 | 113.0067 | 113.2378
2001-01-16 18:18 | 119.44 | 2001-01-15 00:07 | 44:11 | 117.4967 | 116.95
2001-01-16 18:23 | 136.99 | 2001-01-15 00:07 | 44:16 | 120.3467 | 120.9544
2001-01-16 18:28 | 138.09 | 2001-01-15 00:07 | 44:21 | 125.02 | 124.1967
2001-01-16 18:33 | 135.91 | 2001-01-15 00:07 | 44:26 | 127.2233 | 126.2911
2001-01-16 18:38 | 139.21 | 2001-01-15 00:07 | 44:31 | 126.63 | 125.6611
2001-01-16 18:43 | 115.15 | 2001-01-15 00:07 | 44:36 | 123.13 | 123.9756
2001-01-16 18:48 | 96.73 | 2001-01-15 00:07 | 44:41 | 122.1667 | 122.6856
2001-01-16 18:53 | 106.31 | 2001-01-15 00:07 | 44:46 | 122.76 | 120.7356
2001-01-16 18:58 | 119.44 | 2001-01-15 00:07 | 44:51 | 117.28 | 116.4344
2001-01-16 19:03 | 126.79 | 2001-01-15 00:07 | 44:56 | 109.2633 | 109.6944
2001-01-16 19:08 | 133.79 | 2001-01-15 00:07 | 45:01 | 102.54 | 104.4489
2001-01-16 19:13 | 138.09 | 2001-01-15 00:07 | 45:06 | 101.5433 | 101.8756
2001-01-16 19:18 | 140.34 | 2001-01-15 00:07 | 45:11 | 101.5433 | 101.79
2001-01-16 19:23 | 115.15 | 2001-01-15 00:07 | 45:16 | 102.2833 | 102.3689
2001-01-16 19:28 | 89.12 | 2001-01-15 00:07 | 45:21 | 103.28 | 103.5356
2001-01-16 19:33 | 91.84 | 2001-01-15 00:07 | 45:26 | 105.0433 | 105.4089
2001-01-16 19:38 | 95.31 | 2001-01-15 00:07 | 45:31 | 107.9033 | 109.0811
2001-01-16 19:43 | 98.15 | 2001-01-15 00:07 | 45:36 | 114.2967 | 114.25
2001-01-16 19:48 | 102.53 | 2001-01-15 00:07 | 45:41 | 120.55 | 117.7644
2001-01-16 19:53 | 104.02 | 2001-01-15 00:07 | 45:46 | 118.4467 | 116.5211
2001-01-16 19:58 | 104.78 | 2001-01-15 00:07 | 45:51 | 110.5667 | 111.46
2001-01-16 20:03 | 106.31 | 2001-01-15 00:07 | 45:56 | 105.3667 | 107.3578
2001-01-16 20:08 | 108.65 | 2001-01-15 00:07 | 46:01 | 106.14 | 107.8133
2001-01-16 20:13 | 112.67 | 2001-01-15 00:07 | 46:06 | 111.9333 | 110.0911
2001-01-16 20:18 | 117.7 | 2001-01-15 00:07 | 46:11 | 112.2 | 114.3211
2001-01-16 20:23 | 122.12 | 2001-01-15 00:07 | 46:16 | 118.83 | 118.2922
2001-01-16 20:28 | 121.22 | 2001-01-15 00:07 | 46:21 | 123.8467 | 125.0578
2001-01-16 20:33 | 131.72 | 2001-01-15 00:07 | 46:26 | 132.4967 | 131.14
2001-01-16 20:38 | 128.73 | 2001-01-15 00:07 | 46:31 | 137.0767 | 133.3189
2001-01-16 20:43 | 119.44 | 2001-01-15 00:07 | 46:36 | 130.3833 | 128.7033
2001-01-16 20:48 | 121.22 | 2001-01-15 00:07 | 46:41 | 118.65 | 117.5089
2001-01-16 20:53 | 125.84 | 2001-01-15 00:07 | 46:46 | 103.4933 | 106.3844
2001-01-16 20:58 | 121.22 | 2001-01-15 00:07 | 46:51 | 97.01 | 97.99
2001-01-16 21:03 | 104.78 | 2001-01-15 00:07 | 46:56 | 93.4667 | 93.8811
2001-01-16 21:08 | 101.79 | 2001-01-15 00:07 | 47:01 | 91.1667 | 91.3278
2001-01-16 21:13 | 101.05 | 2001-01-15 00:07 | 47:06 | 89.35 | 89.43
2001-01-16 21:18 | 101.79 | 2001-01-15 00:07 | 47:11 | 87.7733 | 87.9267
2001-01-16 21:23 | 101.79 | 2001-01-15 00:07 | 47:16 | 86.6567 | 86.5133
2001-01-16 21:28 | 103.27 | 2001-01-15 00:07 | 47:21 | 85.11 | 85.0433
2001-01-16 21:33 | 104.78 | 2001-01-15 00:07 | 47:26 | 83.3633 | 83.2211
2001-01-16 21:38 | 107.08 | 2001-01-15 00:07 | 47:31 | 81.19 | 81.4122
2001-01-16 21:43 | 111.85 | 2001-01-15 00:07 | 47:36 | 79.6833 | 79.8278
2001-01-16 21:48 | 123.96 | 2001-01-15 00:07 | 47:41 | 78.61 | 78.8256
2001-01-16 21:53 | 125.84 | 2001-01-15 00:07 | 47:46 | 78.1833 | 78.1822
2001-01-16 21:58 | 105.54 | 2001-01-15 00:07 | 47:51 | 77.7533 | 77.8244
2001-01-16 22:03 | 100.32 | 2001-01-15 00:07 | 47:56 | 77.5367 | 77.5367
2001-01-16 22:08 | 110.24 | 2001-01-15 00:07 | 48:01 | 77.32 | 77.3211
2001-01-16 22:13 | 107.86 | 2001-01-15 00:07 | 48:06 | 77.1067 | 77.1067
2001-01-16 22:18 | 117.7 | 2001-01-15 00:07 | 48:11 | 76.8933 | 76.8933
2001-01-16 22:23 | 111.04 | 2001-01-15 00:07 | 48:16 | 76.68 | 76.6789
2001-01-16 22:28 | 127.75 | 2001-01-15 00:07 | 48:21 | 76.4633 | 76.4633
2001-01-16 22:33 | 132.75 | 2001-01-15 00:07 | 48:26 | 76.2467 | 76.2467
2001-01-16 22:38 | 136.99 | 2001-01-15 00:07 | 48:31 | 76.03 | 76.0311
2001-01-16 22:43 | 141.49 | 2001-01-15 00:07 | 48:36 | 75.8167 | 75.8167
2001-01-16 22:48 | 112.67 | 2001-01-15 00:07 | 48:41 | 75.6033 | 75.5311
2001-01-16 22:53 | 101.79 | 2001-01-15 00:07 | 48:46 | 75.1733 | 75.2444
2001-01-16 22:58 | 96.02 | 2001-01-15 00:07 | 48:51 | 74.9567 | 74.9567
2001-01-16 23:03 | 93.22 | 2001-01-15 00:07 | 48:56 | 74.74 | 74.8122
2001-01-16 23:08 | 91.16 | 2001-01-15 00:07 | 49:01 | 74.74 | 74.6689
2001-01-16 23:13 | 89.12 | 2001-01-15 00:07 | 49:06 | 74.5267 | 74.5267
2001-01-16 23:18 | 87.77 | 2001-01-15 00:07 | 49:11 | 74.3133 | 74.3133
2001-01-16 23:23 | 86.43 | 2001-01-15 00:07 | 49:16 | 74.1 | 74.2422
2001-01-16 23:28 | 85.77 | 2001-01-15 00:07 | 49:21 | 74.3133 | 74.4567
2001-01-16 23:33 | 83.13 | 2001-01-15 00:07 | 49:26 | 74.9567 | 74.9567
2001-01-16 23:38 | 81.19 | 2001-01-15 00:07 | 49:31 | 75.6 | 75.5289
2001-01-16 23:43 | 79.25 | 2001-01-15 00:07 | 49:36 | 76.03 | 75.8156
2001-01-16 23:48 | 78.61 | 2001-01-15 00:07 | 49:41 | 75.8167 | 75.7444
2001-01-16 23:53 | 77.97 | 2001-01-15 00:07 | 49:46 | 75.3867 | 75.3156
2001-01-16 23:58 | 77.97 | 2001-01-15 00:07 | 49:51 | 74.7433 | 74.8144
2001-01-17 00:03 | 77.32 | 2001-01-15 00:07 | 49:56 | 74.3133 | 74.3856
2001-01-17 00:08 | 77.32 | 2001-01-15 00:07 | 50:01 | 74.1 | 74.1011
2001-01-17 00:13 | 77.32 | 2001-01-15 00:07 | 50:06 | 73.89 | 73.89
2001-01-17 00:18 | 76.68 | 2001-01-15 00:07 | 50:11 | 73.68 | 73.6089
2001-01-17 00:23 | 76.68 | 2001-01-15 00:07 | 50:16 | 73.2567 | 73.3267
2001-01-17 00:28 | 76.68 | 2001-01-15 00:07 | 50:21 | 73.0433 | 73.0433
2001-01-17 00:33 | 76.03 | 2001-01-15 00:07 | 50:26 | 72.83 | 72.9011
2001-01-17 00:38 | 76.03 | 2001-01-15 00:07 | 50:31 | 72.83 | 72.83
2001-01-17 00:43 | 76.03 | 2001-01-15 00:07 | 50:36 | 72.83 | 72.83
2001-01-17 00:48 | 75.39 | 2001-01-15 00:07 | 50:41 | 72.83 | 72.83
2001-01-17 00:53 | 75.39 | 2001-01-15 00:07 | 50:46 | 72.83 | 72.76
2001-01-17 00:58 | 74.74 | 2001-01-15 00:07 | 50:51 | 72.62 | 72.69
2001-01-17 01:03 | 74.74 | 2001-01-15 00:07 | 50:56 | 72.62 | 72.55
2001-01-17 01:08 | 74.74 | 2001-01-15 00:07 | 51:01 | 72.41 | 72.48
2001-01-17 01:13 | 74.74 | 2001-01-15 00:07 | 51:06 | 72.41 | 72.34
2001-01-17 01:18 | 74.1 | 2001-01-15 00:07 | 51:11 | 72.2 | 72.34
2001-01-17 01:23 | 74.1 | 2001-01-15 00:07 | 51:16 | 72.41 | 72.41
2001-01-17 01:28 | 74.1 | 2001-01-15 00:07 | 51:21 | 72.62 | 72.62
2001-01-17 01:33 | 74.74 | 2001-01-15 00:07 | 51:26 | 72.83 | 72.76
2001-01-17 01:38 | 76.03 | 2001-01-15 00:07 | 51:31 | 72.83 | 72.76
2001-01-17 01:43 | 76.03 | 2001-01-15 00:07 | 51:36 | 72.62 | 72.62
2001-01-17 01:48 | 76.03 | 2001-01-15 00:07 | 51:41 | 72.41 | 72.41
2001-01-17 01:53 | 75.39 | 2001-01-15 00:07 | 51:46 | 72.2 | 72.27
2001-01-17 01:58 | 74.74 | 2001-01-15 00:07 | 51:51 | 72.2 | 72.13
2001-01-17 02:03 | 74.1 | 2001-01-15 00:07 | 51:56 | 71.99 | 71.99
2001-01-17 02:08 | 74.1 | 2001-01-15 00:07 | 52:01 | 71.78 | 71.78
2001-01-17 02:13 | 74.1 | 2001-01-15 00:07 | 52:06 | 71.57 | 71.71
2001-01-17 02:18 | 73.47 | 2001-01-15 00:07 | 52:11 | 71.78 | 71.78
2001-01-17 02:23 | 73.47 | 2001-01-15 00:07 | 52:16 | 71.99 | 71.92
2001-01-17 02:28 | 72.83 | 2001-01-15 00:07 | 52:21 | 71.99 | 71.92
2001-01-17 02:33 | 72.83 | 2001-01-15 00:07 | 52:26 | 71.78 | 71.78
2001-01-17 02:38 | 72.83 | 2001-01-15 00:07 | 52:31 | 71.57 | 71.64
2001-01-17 02:43 | 72.83 | 2001-01-15 00:07 | 52:36 | 71.57 | 71.5011
2001-01-17 02:48 | 72.83 | 2001-01-15 00:07 | 52:41 | 71.3633 | 71.3633
2001-01-17 02:53 | 72.83 | 2001-01-15 00:07 | 52:46 | 71.1567 | 71.1567
2001-01-17 02:58 | 72.83 | 2001-01-15 00:07 | 52:51 | 70.95 | 71.0189
2001-01-17 03:03 | 72.2 | 2001-01-15 00:07 | 52:56 | 70.95 | 71.0189
2001-01-17 03:08 | 72.83 | 2001-01-15 00:07 | 53:01 | 71.1567 | 71.1567
2001-01-17 03:13 | 72.2 | 2001-01-15 00:07 | 53:06 | 71.3633 | 71.4333
2001-01-17 03:18 | 72.2 | 2001-01-15 00:07 | 53:11 | 71.78 | 71.7111
2001-01-17 03:23 | 72.2 | 2001-01-15 00:07 | 53:16 | 71.99 | 71.99
2001-01-17 03:28 | 72.83 | 2001-01-15 00:07 | 53:21 | 72.2 | 72.13
2001-01-17 03:33 | 72.83 | 2001-01-15 00:07 | 53:26 | 72.2 | 72.2
2001-01-17 03:38 | 72.83 | 2001-01-15 00:07 | 53:31 | 72.2 | 72.2
2001-01-17 03:43 | 72.83 | 2001-01-15 00:07 | 53:36 | 72.2 | 72.2
2001-01-17 03:48 | 72.2 | 2001-01-15 00:07 | 53:41 | 72.2 | 72.13
2001-01-17 03:53 | 72.2 | 2001-01-15 00:07 | 53:46 | 71.99 | 71.99
2001-01-17 03:58 | 72.2 | 2001-01-15 00:07 | 53:51 | 71.78 | 71.78
2001-01-17 04:03 | 72.2 | 2001-01-15 00:07 | 53:56 | 71.57 | 71.64
2001-01-17 04:08 | 71.57 | 2001-01-15 00:07 | 54:01 | 71.57 | 71.64
2001-01-17 04:13 | 71.57 | 2001-01-15 00:07 | 54:06 | 71.78 | 71.78
2001-01-17 04:18 | 71.57 | 2001-01-15 00:07 | 54:11 | 71.99 | 71.99
2001-01-17 04:23 | 72.2 | 2001-01-15 00:07 | 54:16 | 72.2 | 72.2
2001-01-17 04:28 | 72.2 | 2001-01-15 00:07 | 54:21 | 72.41 | 72.4811
2001-01-17 04:33 | 71.57 | 2001-01-15 00:07 | 54:26 | 72.8333 | 72.9033
2001-01-17 04:38 | 71.57 | 2001-01-15 00:07 | 54:31 | 73.4667 | 73.3967
2001-01-17 04:43 | 71.57 | 2001-01-15 00:07 | 54:36 | 73.89 | 74.6067
2001-01-17 04:48 | 71.57 | 2001-01-15 00:07 | 54:41 | 76.4633 | 77.5767
2001-01-17 04:53 | 70.95 | 2001-01-15 00:07 | 54:46 | 82.3767 | 83.73
2001-01-17 04:58 | 70.95 | 2001-01-15 00:07 | 54:51 | 92.35 | 92.6144
2001-01-17 05:03 | 70.95 | 2001-01-15 00:07 | 54:56 | 103.1167 | 102.4011
2001-01-17 05:08 | 70.95 | 2001-01-15 00:07 | 55:01 | 111.7367 | 110.9767
2001-01-17 05:13 | 71.57 | 2001-01-15 00:07 | 55:06 | 118.0767 | 117.8767
2001-01-17 05:18 | 71.57 | 2001-01-15 00:07 | 55:11 | 123.8167 | 122.9133
2001-01-17 05:23 | 72.2 | 2001-01-15 00:07 | 55:16 | 126.8467 | 122.2178
2001-01-17 05:28 | 72.2 | 2001-01-15 00:07 | 55:21 | 115.99 | 116.1511
2001-01-17 05:33 | 72.2 | 2001-01-15 00:07 | 55:26 | 105.6167 | 106.5444
2001-01-17 05:38 | 72.2 | 2001-01-15 00:07 | 55:31 | 98.0267 | 102.7533
2001-01-17 05:43 | 72.2 | 2001-01-15 00:07 | 55:36 | 104.6167 | 103.6033
2001-01-17 05:48 | 72.2 | 2001-01-15 00:07 | 55:41 | 108.1667 | 107.5856
2001-01-17 05:53 | 72.2 | 2001-01-15 00:07 | 55:46 | 109.9733 | 110.1044
2001-01-17 05:58 | 71.57 | 2001-01-15 00:07 | 55:51 | 112.1733 | 112.9644
2001-01-17 06:03 | 71.57 | 2001-01-15 00:07 | 55:56 | 116.7467 | 116.7333
2001-01-17 06:08 | 71.57 | 2001-01-15 00:07 | 56:01 | 121.28 | 118.5133
2001-01-17 06:13 | 71.57 | 2001-01-15 00:07 | 56:06 | 117.5133 | 116.47
2001-01-17 06:18 | 72.2 | 2001-01-15 00:07 | 56:11 | 110.6167 | 111.5822
2001-01-17 06:23 | 72.2 | 2001-01-15 00:07 | 56:16 | 106.6167 | 108.6511
2001-01-17 06:28 | 72.2 | 2001-01-15 00:07 | 56:21 | 108.72 | 108.5289
2001-01-17 06:33 | 72.83 | 2001-01-15 00:07 | 56:26 | 110.25 | 110.48
2001-01-17 06:38 | 73.47 | 2001-01-15 00:07 | 56:31 | 112.47 | 112.0967
2001-01-17 06:43 | 74.1 | 2001-01-15 00:07 | 56:36 | 113.57 | 114.3933
2001-01-17 06:48 | 74.1 | 2001-01-15 00:07 | 56:41 | 117.14 | 115.3
2001-01-17 06:53 | 81.19 | 2001-01-15 00:07 | 56:46 | 115.19 | 113.4033
2001-01-17 06:58 | 91.84 | 2001-01-15 00:07 | 56:51 | 107.88 | 108.0478
2001-01-17 07:03 | 104.02 | 2001-01-15 00:07 | 56:56 | 101.0733 | 102.2244
2001-01-17 07:08 | 113.49 | 2001-01-15 00:07 | 57:01 | 97.72 | 100.2922
2001-01-17 07:13 | 117.7 | 2001-01-15 00:07 | 57:06 | 102.0833 | 102.0611
2001-01-17 07:18 | 123.04 | 2001-01-15 00:07 | 57:11 | 106.38 | 106.34
2001-01-17 07:23 | 130.71 | 2001-01-15 00:07 | 57:16 | 110.5567 | 110.5267
2001-01-17 07:28 | 126.79 | 2001-01-15 00:07 | 57:21 | 114.6433 | 114.4122
2001-01-17 07:33 | 90.47 | 2001-01-15 00:07 | 57:26 | 118.0367 | 116.8133
2001-01-17 07:38 | 99.59 | 2001-01-15 00:07 | 57:31 | 117.76 | 115.5833
2001-01-17 07:43 | 104.02 | 2001-01-15 00:07 | 57:36 | 110.9533 | 108.8456
2001-01-17 07:48 | 110.24 | 2001-01-15 00:07 | 57:41 | 97.8233 | 99.6422
2001-01-17 07:53 | 110.24 | 2001-01-15 00:07 | 57:46 | 90.15 | 92.0833
2001-01-17 07:58 | 109.44 | 2001-01-15 00:07 | 57:51 | 88.2767 | 91.0367
2001-01-17 08:03 | 116.84 | 2001-01-15 00:07 | 57:56 | 94.6833 | 95.1978
2001-01-17 08:08 | 123.96 | 2001-01-15 00:07 | 58:01 | 102.6333 | 104.6844
2001-01-17 08:13 | 123.04 | 2001-01-15 00:07 | 58:06 | 116.7367 | 113.4178
2001-01-17 08:18 | 105.54 | 2001-01-15 00:07 | 58:11 | 120.8833 | 118.1089
2001-01-17 08:23 | 103.27 | 2001-01-15 00:07 | 58:16 | 116.7067 | 114.8433
2001-01-17 08:28 | 111.04 | 2001-01-15 00:07 | 58:21 | 106.94 | 109.1433
2001-01-17 08:33 | 111.85 | 2001-01-15 00:07 | 58:26 | 103.7833 | 107.1967
2001-01-17 08:38 | 107.86 | 2001-01-15 00:07 | 58:31 | 110.8667 | 108.0067
2001-01-17 08:43 | 117.7 | 2001-01-15 00:07 | 58:36 | 109.37 | 109.3767
2001-01-17 08:48 | 115.15 | 2001-01-15 00:07 | 58:41 | 107.8933 | 106.1067
2001-01-17 08:53 | 118.57 | 2001-01-15 00:07 | 58:46 | 101.0567 | 102.8556
2001-01-17 08:58 | 111.85 | 2001-01-15 00:07 | 58:51 | 99.6167 | 101.0156
2001-01-17 09:03 | 93.22 | 2001-01-15 00:07 | 58:56 | 102.3733 | 101.5367
2001-01-17 09:08 | 98.15 | 2001-01-15 00:07 | 59:01 | 102.62 | 102.9367
2001-01-17 09:13 | 101.79 | 2001-01-15 00:07 | 59:06 | 103.8167 | 103.3311
2001-01-17 09:18 | 106.31 | 2001-01-15 00:07 | 59:11 | 103.5567 | 104.4178
2001-01-17 09:23 | 111.04 | 2001-01-15 00:07 | 59:16 | 105.88 | 106.1189
2001-01-17 09:28 | 114.32 | 2001-01-15 00:07 | 59:21 | 108.92 | 108.6189
2001-01-17 09:33 | 118.57 | 2001-01-15 00:07 | 59:26 | 111.0567 | 110.08
2001-01-17 09:38 | 121.22 | 2001-01-15 00:07 | 59:31 | 110.2633 | 110.18
2001-01-17 09:43 | 113.49 | 2001-01-15 00:07 | 59:36 | 109.22 | 109.1178
2001-01-17 09:48 | 98.15 | 2001-01-15 00:07 | 59:41 | 107.87 | 108.6733
2001-01-17 09:53 | 81.83 | 2001-01-15 00:07 | 59:46 | 108.93 | 109.8422
2001-01-17 09:58 | 90.47 | 2001-01-15 00:07 | 59:51 | 112.7267 | 111.9111
2001-01-17 10:03 | 92.53 | 2001-01-15 00:07 | 59:56 | 114.0767 | 112.9311
2001-01-17 10:08 | 101.05 | 2001-01-15 00:07 | 60:01 | 111.99 | 110.5933
2001-01-17 10:13 | 114.32 | 2001-01-15 00:07 | 60:06 | 105.7133 | 106.0222
2001-01-17 10:18 | 134.84 | 2001-01-15 00:07 | 60:11 | 100.3633 | 101.49
2001-01-17 10:23 | 113.49 | 2001-01-15 00:07 | 60:16 | 98.3933 | 99.4567
2001-01-17 10:28 | 101.79 | 2001-01-15 00:07 | 60:21 | 99.6133 | 100.1922
2001-01-17 10:33 | 105.54 | 2001-01-15 00:07 | 60:26 | 102.57 | 102.3256
2001-01-17 10:38 | 104.02 | 2001-01-15 00:07 | 60:31 | 104.7933 | 103.97
2001-01-17 10:43 | 123.04 | 2001-01-15 00:07 | 60:36 | 104.5467 | 103.2522
2001-01-17 10:48 | 101.05 | 2001-01-15 00:07 | 60:41 | 100.4167 | 100.8933
2001-01-17 10:53 | 99.59 | 2001-01-15 00:07 | 60:46 | 97.7167 | 99.2911
2001-01-17 10:58 | 102.53 | 2001-01-15 00:07 | 60:51 | 99.74 | 100.2722
2001-01-17 11:03 | 96.73 | 2001-01-15 00:07 | 60:56 | 103.36 | 103.9367
2001-01-17 11:08 | 107.86 | 2001-01-15 00:07 | 61:01 | 108.71 | 107.0144
2001-01-17 11:13 | 103.27 | 2001-01-15 00:07 | 61:06 | 108.9733 | 110.0378
2001-01-17 11:18 | 100.32 | 2001-01-15 00:07 | 61:11 | 112.43 | 110.74
2001-01-17 11:23 | 107.08 | 2001-01-15 00:07 | 61:16 | 110.8167 | 112.8511
2001-01-17 11:28 | 110.24 | 2001-01-15 00:07 | 61:21 | 115.3067 | 115.7656
2001-01-17 11:33 | 109.44 | 2001-01-15 00:07 | 61:26 | 121.1733 | 118.7033
2001-01-17 11:38 | 113.49 | 2001-01-15 00:07 | 61:31 | 119.63 | 118.4733
2001-01-17 11:43 | 107.86 | 2001-01-15 00:07 | 61:36 | 114.6167 | 113.61
2001-01-17 11:48 | 106.31 | 2001-01-15 00:07 | 61:41 | 106.5833 | 110.3133
2001-01-17 11:53 | 109.44 | 2001-01-15 00:07 | 61:46 | 109.74 | 108.8622
2001-01-17 11:58 | 111.04 | 2001-01-15 00:07 | 61:51 | 110.2633 | 110.0011
2001-01-17 12:03 | 117.7 | 2001-01-15 00:07 | 61:56 | 110 | 109.7267
2001-01-17 12:08 | 113.49 | 2001-01-15 00:07 | 62:01 | 108.9167 | 109.6333
2001-01-17 12:13 | 104.78 | 2001-01-15 00:07 | 62:06 | 109.9833 | 108.7089
2001-01-17 12:18 | 98.87 | 2001-01-15 00:07 | 62:11 | 107.2267 | 107.1244
2001-01-17 12:23 | 97.44 | 2001-01-15 00:07 | 62:16 | 104.1633 | 104.0667
2001-01-17 12:28 | 98.87 | 2001-01-15 00:07 | 62:21 | 100.81 | 102.9344
2001-01-17 12:33 | 102.53 | 2001-01-15 00:07 | 62:26 | 103.83 | 103.4078
2001-01-17 12:38 | 106.31 | 2001-01-15 00:07 | 62:31 | 105.5833 | 105.6733
2001-01-17 12:43 | 105.54 | 2001-01-15 00:07 | 62:36 | 107.6067 | 107.1089
2001-01-17 12:48 | 101.79 | 2001-01-15 00:07 | 62:41 | 108.1367 | 109.6167
2001-01-17 12:53 | 93.92 | 2001-01-15 00:07 | 62:46 | 113.1067 | 112.0756
2001-01-17 12:58 | 97.44 | 2001-01-15 00:07 | 62:51 | 114.9833 | 114.7189
2001-01-17 13:03 | 107.86 | 2001-01-15 00:07 | 62:56 | 116.0667 | 114.8467
2001-01-17 13:08 | 104.78 | 2001-01-15 00:07 | 63:01 | 113.49 | 112.2511
2001-01-17 13:13 | 113.49 | 2001-01-15 00:07 | 63:06 | 107.1967 | 107.2744
2001-01-17 13:18 | 108.65 | 2001-01-15 00:07 | 63:11 | 101.1367 | 101.2156
2001-01-17 13:23 | 115.15 | 2001-01-15 00:07 | 63:16 | 95.3133 | 97.6478
2001-01-17 13:28 | 108.65 | 2001-01-15 00:07 | 63:21 | 96.4933 | 96.82
2001-01-17 13:33 | 122.12 | 2001-01-15 00:07 | 63:26 | 98.6533 | 99.1622
2001-01-17 13:38 | 132.75 | 2001-01-15 00:07 | 63:31 | 102.34 | 103.2833
2001-01-17 13:43 | 104.02 | 2001-01-15 00:07 | 63:36 | 108.8567 | 108.7444
2001-01-17 13:48 | 107.08 | 2001-01-15 00:07 | 63:41 | 115.0367 | 114.9556
2001-01-17 13:53 | 108.65 | 2001-01-15 00:07 | 63:46 | 120.9733 | 120.22
2001-01-17 13:58 | 113.49 | 2001-01-15 00:07 | 63:51 | 124.65 | 123.5233
2001-01-17 14:03 | 108.65 | 2001-01-15 00:07 | 63:56 | 124.9467 | 124.44
2001-01-17 14:08 | 107.86 | 2001-01-15 00:07 | 64:01 | 123.7233 | 123.7044
2001-01-17 14:13 | 110.24 | 2001-01-15 00:07 | 64:06 | 122.4433 | 123.8133
2001-01-17 14:18 | 111.85 | 2001-01-15 00:07 | 64:11 | 125.2733 | 124.6344
2001-01-17 14:23 | 99.59 | 2001-01-15 00:07 | 64:16 | 126.1867 | 124.8933
2001-01-17 14:28 | 101.05 | 2001-01-15 00:07 | 64:21 | 123.22 | 124.32
2001-01-17 14:33 | 101.79 | 2001-01-15 00:07 | 64:26 | 123.5533 | 123.4422
2001-01-17 14:38 | 108.65 | 2001-01-15 00:07 | 64:31 | 123.5533 | 125.1889
2001-01-17 14:43 | 106.31 | 2001-01-15 00:07 | 64:36 | 128.46 | 127.4022
2001-01-17 14:48 | 107.86 | 2001-01-15 00:07 | 64:41 | 130.1933 | 131.1856
2001-01-17 14:53 | 110.24 | 2001-01-15 00:07 | 64:46 | 134.9033 | 134.2778
2001-01-17 14:58 | 121.22 | 2001-01-15 00:07 | 64:51 | 137.7367 | 136.6733
2001-01-17 15:03 | 113.49 | 2001-01-15 00:07 | 64:56 | 137.38 | 137.0211
2001-01-17 15:08 | 113.49 | 2001-01-15 00:07 | 65:01 | 135.9467 | 132.9411
2001-01-17 15:13 | 113.49 | 2001-01-15 00:07 | 65:06 | 125.4967 | 124.6667
2001-01-17 15:18 | 94.61 | 2001-01-15 00:07 | 65:11 | 112.5567 | 112.1333
2001-01-17 15:23 | 95.31 | 2001-01-15 00:07 | 65:16 | 98.3467 | 100.8511
2001-01-17 15:28 | 96.02 | 2001-01-15 00:07 | 65:21 | 91.65 | 93.5711
2001-01-17 15:33 | 98.15 | 2001-01-15 00:07 | 65:26 | 90.7167 | 91.5678
2001-01-17 15:38 | 101.79 | 2001-01-15 00:07 | 65:31 | 92.3367 | 93.11
2001-01-17 15:43 | 107.08 | 2001-01-15 00:07 | 65:36 | 96.2767 | 96.4178
2001-01-17 15:48 | 117.7 | 2001-01-15 00:07 | 65:41 | 100.64 | 100.6767
2001-01-17 15:53 | 120.33 | 2001-01-15 00:07 | 65:46 | 105.1133 | 105.0756
2001-01-17 15:58 | 124.89 | 2001-01-15 00:07 | 65:51 | 109.4733 | 110.5111
2001-01-17 16:03 | 128.73 | 2001-01-15 00:07 | 65:56 | 116.9467 | 117.0456
2001-01-17 16:08 | 121.22 | 2001-01-15 00:07 | 66:01 | 124.7167 | 125.2011
2001-01-17 16:13 | 121.22 | 2001-01-15 00:07 | 66:06 | 133.94 | 132.1556
2001-01-17 16:18 | 124.89 | 2001-01-15 00:07 | 66:11 | 137.81 | 137.2378
2001-01-17 16:23 | 129.71 | 2001-01-15 00:07 | 66:16 | 139.9633 | 138.9956
2001-01-17 16:28 | 123.96 | 2001-01-15 00:07 | 66:21 | 139.2133 | 136.48
2001-01-17 16:33 | 115.99 | 2001-01-15 00:07 | 66:26 | 130.2633 | 130.4811
2001-01-17 16:38 | 130.71 | 2001-01-15 00:07 | 66:31 | 121.9667 | 123.06
2001-01-17 16:43 | 123.96 | 2001-01-15 00:07 | 66:36 | 116.95 | 118.9944
2001-01-17 16:48 | 130.71 | 2001-01-15 00:07 | 66:41 | 118.0667 | 118.8689
2001-01-17 16:53 | 135.91 | 2001-01-15 00:07 | 66:46 | 121.59 | 120.7267
2001-01-17 16:58 | 138.09 | 2001-01-15 00:07 | 66:51 | 122.5233 | 123.8656
2001-01-17 17:03 | 139.21 | 2001-01-15 00:07 | 66:56 | 127.4833 | 127.4211
2001-01-17 17:08 | 134.84 | 2001-01-15 00:07 | 67:01 | 132.2567 | 131.9044
2001-01-17 17:13 | 133.79 | 2001-01-15 00:07 | 67:06 | 135.9733 | 135.32
2001-01-17 17:18 | 107.86 | 2001-01-15 00:07 | 67:11 | 137.73 | 137.1444
2001-01-17 17:23 | 96.02 | 2001-01-15 00:07 | 67:16 | 137.73 | 138.1022
2001-01-17 17:28 | 91.16 | 2001-01-15 00:07 | 67:21 | 138.8467 | 138.5967
2001-01-17 17:33 | 87.77 | 2001-01-15 00:07 | 67:26 | 139.2133 | 136.1422
2001-01-17 17:38 | 93.22 | 2001-01-15 00:07 | 67:31 | 130.3667 | 130.3322
2001-01-17 17:43 | 96.02 | 2001-01-15 00:07 | 67:36 | 121.4167 | 122.2311
2001-01-17 17:48 | 99.59 | 2001-01-15 00:07 | 67:41 | 114.91 | 117.3544
2001-01-17 17:53 | 106.31 | 2001-01-15 00:07 | 67:46 | 115.7367 | 114.9233
2001-01-17 17:58 | 109.44 | 2001-01-15 00:07 | 67:51 | 114.1233 | 113.4711
2001-01-17 18:03 | 112.67 | 2001-01-15 00:07 | 67:56 | 110.5533 | 111.5589
2001-01-17 18:08 | 128.73 | 2001-01-15 00:07 | 68:01 | 110 | 111.4822
2001-01-17 18:13 | 132.75 | 2001-01-15 00:07 | 68:06 | 113.8933 | 115.3611
2001-01-17 18:18 | 140.34 | 2001-01-15 00:07 | 68:11 | 122.19 | 123.0678
2001-01-17 18:23 | 140.34 | 2001-01-15 00:07 | 68:16 | 133.12 | 130.63
2001-01-17 18:28 | 139.21 | 2001-01-15 00:07 | 68:21 | 136.58 | 134.98
2001-01-17 18:33 | 138.09 | 2001-01-15 00:07 | 68:26 | 135.24 | 134.0689
2001-01-17 18:38 | 113.49 | 2001-01-15 00:07 | 68:31 | 130.3867 | 131.6756
2001-01-17 18:43 | 114.32 | 2001-01-15 00:07 | 68:36 | 129.4 | 130.0611
2001-01-17 18:48 | 123.04 | 2001-01-15 00:07 | 68:41 | 130.3967 | 130.2944
2001-01-17 18:53 | 116.84 | 2001-01-15 00:07 | 68:46 | 131.0867 | 131.8833
2001-01-17 18:58 | 124.89 | 2001-01-15 00:07 | 68:51 | 134.1667 | 133.2544
2001-01-17 19:03 | 125.84 | 2001-01-15 00:07 | 68:56 | 134.51 | 133.6178
2001-01-17 19:08 | 131.72 | 2001-01-15 00:07 | 69:01 | 132.1767 | 131.3022
2001-01-17 19:13 | 139.21 | 2001-01-15 00:07 | 69:06 | 127.22 | 128.21
2001-01-17 19:18 | 136.99 | 2001-01-15 00:07 | 69:11 | 125.2333 | 124.0567
2001-01-17 19:23 | 136.99 | 2001-01-15 00:07 | 69:16 | 119.7167 | 119.6289
2001-01-17 19:28 | 139.21 | 2001-01-15 00:07 | 69:21 | 113.9367 | 113.9356
2001-01-17 19:33 | 140.34 | 2001-01-15 00:07 | 69:26 | 108.1533 | 110.26
2001-01-17 19:38 | 138.09 | 2001-01-15 00:07 | 69:31 | 108.69 | 109.7567
2001-01-17 19:43 | 112.67 | 2001-01-15 00:07 | 69:36 | 112.4267 | 111.9089
2001-01-17 19:48 | 113.49 | 2001-01-15 00:07 | 69:41 | 114.61 | 114.9233
2001-01-17 19:53 | 118.57 | 2001-01-15 00:07 | 69:46 | 117.7333 | 117.5778
2001-01-17 19:58 | 115.15 | 2001-01-15 00:07 | 69:51 | 120.39 | 121.14
2001-01-17 20:03 | 108.65 | 2001-01-15 00:07 | 69:56 | 125.2967 | 123.6611
2001-01-17 20:08 | 107.86 | 2001-01-15 00:07 | 70:01 | 125.2967 | 123.5078
2001-01-17 20:13 | 113.49 | 2001-01-15 00:07 | 70:06 | 119.93 | 119.5333
2001-01-17 20:18 | 120.33 | 2001-01-15 00:07 | 70:11 | 113.3733 | 115.0722
2001-01-17 20:23 | 132.75 | 2001-01-15 00:07 | 70:16 | 111.9133 | 112.6644
2001-01-17 20:28 | 146.28 | 2001-01-15 00:07 | 70:21 | 112.7067 | 112.3533
2001-01-17 20:33 | 130.71 | 2001-01-15 00:07 | 70:26 | 112.44 | 112.0656
2001-01-17 20:38 | 128.73 | 2001-01-15 00:07 | 70:31 | 111.05 | 112.1522
2001-01-17 20:43 | 131.72 | 2001-01-15 00:07 | 70:36 | 112.9667 | 114.3822
2001-01-17 20:48 | 127.75 | 2001-01-15 00:07 | 70:41 | 119.13 | 120.15
2001-01-17 20:53 | 131.72 | 2001-01-15 00:07 | 70:46 | 128.3533 | 127.9844
2001-01-17 20:58 | 133.79 | 2001-01-15 00:07 | 70:51 | 136.47 | 133.1322
2001-01-17 21:03 | 136.99 | 2001-01-15 00:07 | 70:56 | 134.5733 | 131.7722
2001-01-17 21:08 | 132.75 | 2001-01-15 00:07 | 71:01 | 124.2733 | 123.5878
2001-01-17 21:13 | 126.79 | 2001-01-15 00:07 | 71:06 | 111.9167 | 113.35
2001-01-17 21:18 | 122.12 | 2001-01-15 00:07 | 71:11 | 103.86 | 105.0544
2001-01-17 21:23 | 126.79 | 2001-01-15 00:07 | 71:16 | 99.3867 | 99.8389
2001-01-17 21:28 | 110.24 | 2001-01-15 00:07 | 71:21 | 96.27 | 96.5278
2001-01-17 21:33 | 104.78 | 2001-01-15 00:07 | 71:26 | 93.9267 | 94.0911
2001-01-17 21:38 | 109.44 | 2001-01-15 00:07 | 71:31 | 92.0767 | 92.16
2001-01-17 21:43 | 111.85 | 2001-01-15 00:07 | 71:36 | 90.4767 | 90.6322
2001-01-17 21:48 | 115.99 | 2001-01-15 00:07 | 71:41 | 89.3433 | 89.4211
2001-01-17 21:53 | 115.99 | 2001-01-15 00:07 | 71:46 | 88.4433 | 88.4444
2001-01-17 21:58 | 121.22 | 2001-01-15 00:07 | 71:51 | 87.5467 | 87.6222
2001-01-17 22:03 | 123.96 | 2001-01-15 00:07 | 71:56 | 86.8767 | 86.8778
2001-01-17 22:08 | 130.71 | 2001-01-15 00:07 | 72:01 | 86.21 | 86.2844
2001-01-17 22:13 | 121.22 | 2001-01-15 00:07 | 72:06 | 85.7667 | 85.6944
2001-01-17 22:18 | 107.86 | 2001-01-15 00:07 | 72:11 | 85.1067 | 85.1067
2001-01-17 22:23 | 111.04 | 2001-01-15 00:07 | 72:16 | 84.4467 | 84.4478
2001-01-17 22:28 | 116.84 | 2001-01-15 00:07 | 72:21 | 83.79 | 83.79
2001-01-17 22:33 | 110.24 | 2001-01-15 00:07 | 72:26 | 83.1333 | 83.2067
2001-01-17 22:38 | 110.24 | 2001-01-15 00:07 | 72:31 | 82.6967 | 82.6978
2001-01-17 22:43 | 112.67 | 2001-01-15 00:07 | 72:36 | 82.2633 | 82.2644
2001-01-17 22:48 | 115.99 | 2001-01-15 00:07 | 72:41 | 81.8333 | 81.8333
2001-01-17 22:53 | 128.73 | 2001-01-15 00:07 | 72:46 | 81.4033 | 81.4756
2001-01-17 22:58 | 140.34 | 2001-01-15 00:07 | 72:51 | 81.19 | 81.1889
2001-01-17 23:03 | 140.34 | 2001-01-15 00:07 | 72:56 | 80.9733 | 80.9022
2001-01-17 23:08 | 123.04 | 2001-01-15 00:07 | 73:01 | 80.5433 | 80.5433
2001-01-17 23:13 | 109.44 | 2001-01-15 00:07 | 73:06 | 80.1133 | 80.1856
2001-01-17 23:18 | 103.27 | 2001-01-15 00:07 | 73:11 | 79.9 | 79.8989
2001-01-17 23:23 | 98.87 | 2001-01-15 00:07 | 73:16 | 79.6833 | 79.6833
2001-01-17 23:28 | 96.02 | 2001-01-15 00:07 | 73:21 | 79.4667 | 79.4667
2001-01-17 23:33 | 93.92 | 2001-01-15 00:07 | 73:26 | 79.25 | 79.2511
2001-01-17 23:38 | 91.84 | 2001-01-15 00:07 | 73:31 | 79.0367 | 79.0367
2001-01-17 23:43 | 90.47 | 2001-01-15 00:07 | 73:36 | 78.8233 | 78.8233
2001-01-17 23:48 | 89.12 | 2001-01-15 00:07 | 73:41 | 78.61 | 78.6811
2001-01-17 23:53 | 88.44 | 2001-01-15 00:07 | 73:46 | 78.61 | 78.61
2001-01-17 23:58 | 87.77 | 2001-01-15 00:07 | 73:51 | 78.61 | 78.61
2001-01-18 00:03 | 86.43 | 2001-01-15 00:07 | 73:56 | 78.61 | 78.5389
2001-01-18 00:08 | 86.43 | 2001-01-15 00:07 | 74:01 | 78.3967 | 78.3967
2001-01-18 00:13 | 85.77 | 2001-01-15 00:07 | 74:06 | 78.1833 | 78.1833
2001-01-18 00:18 | 85.1 | 2001-01-15 00:07 | 74:11 | 77.97 | 78.0411
2001-01-18 00:23 | 84.45 | 2001-01-15 00:07 | 74:16 | 77.97 | 77.97
2001-01-18 00:28 | 83.79 | 2001-01-15 00:07 | 74:21 | 77.97 | 77.97
2001-01-18 00:33 | 83.13 | 2001-01-15 00:07 | 74:26 | 77.97 | 77.97
2001-01-18 00:38 | 82.48 | 2001-01-15 00:07 | 74:31 | 77.97 | 77.8978
2001-01-18 00:43 | 82.48 | 2001-01-15 00:07 | 74:36 | 77.7533 | 77.7533
2001-01-18 00:48 | 81.83 | 2001-01-15 00:07 | 74:41 | 77.5367 | 77.5367
2001-01-18 00:53 | 81.19 | 2001-01-15 00:07 | 74:46 | 77.32 | 77.3922
2001-01-18 00:58 | 81.19 | 2001-01-15 00:07 | 74:51 | 77.32 | 77.32
2001-01-18 01:03 | 81.19 | 2001-01-15 00:07 | 74:56 | 77.32 | 77.32
2001-01-18 01:08 | 80.54 | 2001-01-15 00:07 | 75:01 | 77.32 | 77.32
2001-01-18 01:13 | 79.9 | 2001-01-15 00:07 | 75:06 | 77.32 | 77.32
2001-01-18 01:18 | 79.9 | 2001-01-15 00:07 | 75:11 | 77.32 | 77.32
2001-01-18 01:23 | 79.9 | 2001-01-15 00:07 | 75:16 | 77.32 | 77.32
2001-01-18 01:28 | 79.25 | 2001-01-15 00:07 | 75:21 | 77.32 | 77.32
2001-01-18 01:33 | 79.25 | 2001-01-15 00:07 | 75:26 | 77.32 | 77.32
2001-01-18 01:38 | 79.25 | 2001-01-15 00:07 | 75:31 | 77.32 | 77.32
2001-01-18 01:43 | 78.61 | 2001-01-15 00:07 | 75:36 | 77.32 | 77.2489
2001-01-18 01:48 | 78.61 | 2001-01-15 00:07 | 75:41 | 77.1067 | 77.1067
2001-01-18 01:53 | 78.61 | 2001-01-15 00:07 | 75:46 | 76.8933 | 76.8933
2001-01-18 01:58 | 78.61 | 2001-01-15 00:07 | 75:51 | 76.68 | 76.7511
2001-01-18 02:03 | 78.61 | 2001-01-15 00:07 | 75:56 | 76.68 | 76.68
2001-01-18 02:08 | 78.61 | 2001-01-15 00:07 | 76:01 | 76.68 | 76.68
2001-01-18 02:13 | 77.97 | 2001-01-15 00:07 | 76:06 | 76.68 | 76.68
2001-01-18 02:18 | 77.97 | 2001-01-15 00:07 | 76:11 | 76.68 | 76.68
2001-01-18 02:23 | 77.97 | 2001-01-15 00:07 | 76:16 | 76.68 | 76.68
2001-01-18 02:28 | 77.97 | 2001-01-15 00:07 | 76:21 | 76.68 | 76.68
2001-01-18 02:33 | 77.97 | 2001-01-15 00:07 | 76:26 | 76.68 | 76.6078
2001-01-18 02:38 | 77.97 | 2001-01-15 00:07 | 76:31 | 76.4633 | 76.32
2001-01-18 02:43 | 77.97 | 2001-01-15 00:07 | 76:36 | 75.8167 | 75.7456
2001-01-18 02:48 | 77.32 | 2001-01-15 00:07 | 76:41 | 74.9567 | 74.9589
2001-01-18 02:53 | 77.32 | 2001-01-15 00:07 | 76:46 | 74.1033 | 74.2467
2001-01-18 02:58 | 77.32 | 2001-01-15 00:07 | 76:51 | 73.68 | 73.7511
2001-01-18 03:03 | 77.32 | 2001-01-15 00:07 | 76:56 | 73.47 | 73.54
2001-01-18 03:08 | 77.32 | 2001-01-15 00:07 | 77:01 | 73.47 | 73.3989
2001-01-18 03:13 | 77.32 | 2001-01-15 00:07 | 77:06 | 73.2567 | 73.2567
2001-01-18 03:18 | 77.32 | 2001-01-15 00:07 | 77:11 | 73.0433 | 73.0433
2001-01-18 03:23 | 77.32 | 2001-01-15 00:07 | 77:16 | 72.83 | 72.8311
2001-01-18 03:28 | 77.32 | 2001-01-15 00:07 | 77:21 | 72.62 | 72.62
2001-01-18 03:33 | 77.32 | 2001-01-15 00:07 | 77:26 | 72.41 | 72.41
2001-01-18 03:38 | 77.32 | 2001-01-15 00:07 | 77:31 | 72.2 | 72.27
2001-01-18 03:43 | 77.32 | 2001-01-15 00:07 | 77:36 | 72.2 | 72.27
2001-01-18 03:48 | 77.32 | 2001-01-15 00:07 | 77:41 | 72.41 | 72.6222
2001-01-18 03:53 | 76.68 | 2001-01-15 00:07 | 77:46 | 73.2567 | 74.7044
2001-01-18 03:58 | 76.68 | 2001-01-15 00:07 | 77:51 | 78.4467 | 79.3722
2001-01-18 04:03 | 76.68 | 2001-01-15 00:07 | 77:56 | 86.4133 | 86.7633
2001-01-18 04:08 | 76.68 | 2001-01-15 00:07 | 78:01 | 95.43 | 94.0644
2001-01-18 04:13 | 76.68 | 2001-01-15 00:07 | 78:06 | 100.35 | 99.6044
2001-01-18 04:18 | 76.68 | 2001-01-15 00:07 | 78:11 | 103.0333 | 102.5556
2001-01-18 04:23 | 76.68 | 2001-01-15 00:07 | 78:16 | 104.2833 | 104.4589
2001-01-18 04:28 | 76.68 | 2001-01-15 00:07 | 78:21 | 106.06 | 105.9856
2001-01-18 04:33 | 76.68 | 2001-01-15 00:07 | 78:26 | 107.6133 | 107.7067
2001-01-18 04:38 | 76.68 | 2001-01-15 00:07 | 78:31 | 109.4467 | 108.3256
2001-01-18 04:43 | 76.03 | 2001-01-15 00:07 | 78:36 | 107.9167 | 109.0611
2001-01-18 04:48 | 74.74 | 2001-01-15 00:07 | 78:41 | 109.82 | 111.5978
2001-01-18 04:53 | 74.1 | 2001-01-15 00:07 | 78:46 | 117.0567 | 118.5133
2001-01-18 04:58 | 73.47 | 2001-01-15 00:07 | 78:51 | 128.6633 | 127.2211
2001-01-18 05:03 | 73.47 | 2001-01-15 00:07 | 78:56 | 135.9433 | 134.2344
2001-01-18 05:08 | 73.47 | 2001-01-15 00:07 | 79:01 | 138.0967 | 137.1367
2001-01-18 05:13 | 73.47 | 2001-01-15 00:07 | 79:06 | 137.37 | 138.1122
2001-01-18 05:18 | 72.83 | 2001-01-15 00:07 | 79:11 | 138.87 | 138.1233
2001-01-18 05:23 | 72.83 | 2001-01-15 00:07 | 79:16 | 138.13 | 138.7433
2001-01-18 05:28 | 72.83 | 2001-01-15 00:07 | 79:21 | 139.23 | 137.0189
2001-01-18 05:33 | 72.2 | 2001-01-15 00:07 | 79:26 | 133.6967 | 131.7944
2001-01-18 05:38 | 72.2 | 2001-01-15 00:07 | 79:31 | 122.4567 | 121.4044
2001-01-18 05:43 | 72.2 | 2001-01-15 00:07 | 79:36 | 108.06 | 109.1111
2001-01-18 05:48 | 72.2 | 2001-01-15 00:07 | 79:41 | 96.8167 | 98.9922
2001-01-18 05:53 | 72.83 | 2001-01-15 00:07 | 79:46 | 92.1 | 92.7556
2001-01-18 05:58 | 74.74 | 2001-01-15 00:07 | 79:51 | 89.35 | 91.53
2001-01-18 06:03 | 87.77 | 2001-01-15 00:07 | 79:56 | 93.14 | 94.1344
2001-01-18 06:08 | 96.73 | 2001-01-15 00:07 | 80:01 | 99.9133 | 100.7911
2001-01-18 06:13 | 101.79 | 2001-01-15 00:07 | 80:06 | 109.32 | 108.0633
2001-01-18 06:18 | 102.53 | 2001-01-15 00:07 | 80:11 | 114.9567 | 115.1122
2001-01-18 06:23 | 104.78 | 2001-01-15 00:07 | 80:16 | 121.06 | 121.4811
2001-01-18 06:28 | 105.54 | 2001-01-15 00:07 | 80:21 | 128.4267 | 127.8011
2001-01-18 06:33 | 107.86 | 2001-01-15 00:07 | 80:26 | 133.9167 | 132.7578
2001-01-18 06:38 | 109.44 | 2001-01-15 00:07 | 80:31 | 135.93 | 131.7278
2001-01-18 06:43 | 111.04 | 2001-01-15 00:07 | 80:36 | 125.3367 | 124.1244
2001-01-18 06:48 | 103.27 | 2001-01-15 00:07 | 80:41 | 111.1067 | 111.2656
2001-01-18 06:53 | 115.15 | 2001-01-15 00:07 | 80:46 | 97.3533 | 100.1778
2001-01-18 06:58 | 132.75 | 2001-01-15 00:07 | 80:51 | 92.0733 | 93.5278
2001-01-18 07:03 | 138.09 | 2001-01-15 00:07 | 80:56 | 91.1567 | 91.3856
2001-01-18 07:08 | 136.99 | 2001-01-15 00:07 | 81:01 | 90.9267 | 91.1556
2001-01-18 07:13 | 139.21 | 2001-01-15 00:07 | 81:06 | 91.3833 | 91.3833
2001-01-18 07:18 | 135.91 | 2001-01-15 00:07 | 81:11 | 91.84 | 90.8667
2001-01-18 07:23 | 141.49 | 2001-01-15 00:07 | 81:16 | 89.3767 | 89.1578
2001-01-18 07:28 | 136.99 | 2001-01-15 00:07 | 81:21 | 86.2567 | 87.45
2001-01-18 07:33 | 139.21 | 2001-01-15 00:07 | 81:26 | 86.7167 | 88.4078
2001-01-18 07:38 | 124.89 | 2001-01-15 00:07 | 81:31 | 92.25 | 92.8833
2001-01-18 07:43 | 103.27 | 2001-01-15 00:07 | 81:36 | 99.6833 | 99.0967
2001-01-18 07:48 | 96.02 | 2001-01-15 00:07 | 81:41 | 105.3567 | 105.3156
2001-01-18 07:53 | 91.16 | 2001-01-15 00:07 | 81:46 | 110.9067 | 111.5022
2001-01-18 07:58 | 89.12 | 2001-01-15 00:07 | 81:51 | 118.2433 | 118.5311
2001-01-18 08:03 | 87.77 | 2001-01-15 00:07 | 81:56 | 126.4433 | 125.3822
2001-01-18 08:08 | 102.53 | 2001-01-15 00:07 | 82:01 | 131.46 | 127.5978
2001-01-18 08:13 | 109.44 | 2001-01-15 00:07 | 82:06 | 124.89 | 124.5256
2001-01-18 08:18 | 115.99 | 2001-01-15 00:07 | 82:11 | 117.2267 | 117.7333
2001-01-18 08:23 | 119.44 | 2001-01-15 00:07 | 82:16 | 111.0833 | 112.7078
2001-01-18 08:28 | 127.75 | 2001-01-15 00:07 | 82:21 | 109.8133 | 109.9689
2001-01-18 08:33 | 138.09 | 2001-01-15 00:07 | 82:26 | 109.01 | 109.1856
2001-01-18 08:38 | 135.91 | 2001-01-15 00:07 | 82:31 | 108.7333 | 110.3333
2001-01-18 08:43 | 133.79 | 2001-01-15 00:07 | 82:36 | 113.2567 | 113.0578
2001-01-18 08:48 | 106.31 | 2001-01-15 00:07 | 82:41 | 117.1833 | 117.7878
2001-01-18 08:53 | 93.22 | 2001-01-15 00:07 | 82:46 | 122.9233 | 123.7489
2001-01-18 08:58 | 92.53 | 2001-01-15 00:07 | 82:51 | 131.14 | 130.5256
2001-01-18 09:03 | 90.47 | 2001-01-15 00:07 | 82:56 | 137.5133 | 136.3333
2001-01-18 09:08 | 90.47 | 2001-01-15 00:07 | 83:01 | 140.3467 | 137.7689
2001-01-18 09:13 | 91.84 | 2001-01-15 00:07 | 83:06 | 135.4467 | 132.8789
2001-01-18 09:18 | 91.84 | 2001-01-15 00:07 | 83:11 | 122.8433 | 122.0122
2001-01-18 09:23 | 91.84 | 2001-01-15 00:07 | 83:16 | 107.7467 | 108.6678
2001-01-18 09:28 | 84.45 | 2001-01-15 00:07 | 83:21 | 95.4133 | 98.0344
2001-01-18 09:33 | 82.48 | 2001-01-15 00:07 | 83:26 | 90.9433 | 92.6667
2001-01-18 09:38 | 93.22 | 2001-01-15 00:07 | 83:31 | 91.6433 | 92.4989
2001-01-18 09:43 | 101.05 | 2001-01-15 00:07 | 83:36 | 94.91 | 95.2289
2001-01-18 09:48 | 104.78 | 2001-01-15 00:07 | 83:41 | 99.1333 | 98.6144
2001-01-18 09:53 | 110.24 | 2001-01-15 00:07 | 83:46 | 101.8 | 102.0944
2001-01-18 09:58 | 117.7 | 2001-01-15 00:07 | 83:51 | 105.35 | 105.6511
2001-01-18 10:03 | 126.79 | 2001-01-15 00:07 | 83:56 | 109.8033 | 110.0322
2001-01-18 10:08 | 134.84 | 2001-01-15 00:07 | 84:01 | 114.9433 | 113.4089
2001-01-18 10:13 | 132.75 | 2001-01-15 00:07 | 84:06 | 115.48 | 114.6667
2001-01-18 10:18 | 107.08 | 2001-01-15 00:07 | 84:11 | 113.5767 | 113.1
2001-01-18 10:23 | 111.85 | 2001-01-15 00:07 | 84:16 | 110.2433 | 109.8322
2001-01-18 10:28 | 114.32 | 2001-01-15 00:07 | 84:21 | 105.6767 | 106.4311
2001-01-18 10:33 | 103.27 | 2001-01-15 00:07 | 84:26 | 103.3733 | 103.6233
2001-01-18 10:38 | 109.44 | 2001-01-15 00:07 | 84:31 | 101.82 | 103.2444
2001-01-18 10:43 | 113.49 | 2001-01-15 00:07 | 84:36 | 104.54 | 104.76
2001-01-18 10:48 | 116.84 | 2001-01-15 00:07 | 84:41 | 107.92 | 109.0278
2001-01-18 10:53 | 121.22 | 2001-01-15 00:07 | 84:46 | 114.6233 | 115.1
2001-01-18 10:58 | 130.71 | 2001-01-15 00:07 | 84:51 | 122.7567 | 122.5089
2001-01-18 11:03 | 141.49 | 2001-01-15 00:07 | 84:56 | 130.1467 | 128.5567
2001-01-18 11:08 | 140.34 | 2001-01-15 00:07 | 85:01 | 132.7667 | 132.12
2001-01-18 11:13 | 139.21 | 2001-01-15 00:07 | 85:06 | 133.4467 | 133.7056
2001-01-18 11:18 | 126.79 | 2001-01-15 00:07 | 85:11 | 134.9033 | 134.8889
2001-01-18 11:23 | 102.53 | 2001-01-15 00:07 | 85:16 | 136.3167 | 136.5633
2001-01-18 11:28 | 93.92 | 2001-01-15 00:07 | 85:21 | 138.47 | 133.4311
2001-01-18 11:33 | 89.79 | 2001-01-15 00:07 | 85:26 | 125.5067 | 125.5922
2001-01-18 11:38 | 89.12 | 2001-01-15 00:07 | 85:31 | 112.8 | 112.6333
2001-01-18 11:43 | 96.02 | 2001-01-15 00:07 | 85:36 | 99.5933 | 104.3233
2001-01-18 11:48 | 99.59 | 2001-01-15 00:07 | 85:41 | 100.5767 | 99.9322
2001-01-18 11:53 | 101.79 | 2001-01-15 00:07 | 85:46 | 99.6267 | 99.4678
2001-01-18 11:58 | 104.02 | 2001-01-15 00:07 | 85:51 | 98.2 | 98.1067
2001-01-18 12:03 | 110.24 | 2001-01-15 00:07 | 85:56 | 96.4933 | 97.9511
2001-01-18 12:08 | 115.15 | 2001-01-15 00:07 | 86:01 | 99.16 | 99.3233
2001-01-18 12:13 | 119.44 | 2001-01-15 00:07 | 86:06 | 102.3167 | 102.1711
2001-01-18 12:18 | 111.85 | 2001-01-15 00:07 | 86:11 | 105.0367 | 104.2989
2001-01-18 12:23 | 109.44 | 2001-01-15 00:07 | 86:16 | 105.5433 | 104.7178
2001-01-18 12:28 | 109.44 | 2001-01-15 00:07 | 86:21 | 103.5733 | 104.7556
2001-01-18 12:33 | 98.15 | 2001-01-15 00:07 | 86:26 | 105.15 | 106.0722
2001-01-18 12:38 | 102.53 | 2001-01-15 00:07 | 86:31 | 109.4933 | 108.6178
2001-01-18 12:43 | 104.78 | 2001-01-15 00:07 | 86:36 | 111.21 | 109.7744
2001-01-18 12:48 | 106.31 | 2001-01-15 00:07 | 86:41 | 108.62 | 109.1967
2001-01-18 12:53 | 112.67 | 2001-01-15 00:07 | 86:46 | 107.76 | 109.9578
2001-01-18 12:58 | 124.89 | 2001-01-15 00:07 | 86:51 | 113.4933 | 113.2822
2001-01-18 13:03 | 130.71 | 2001-01-15 00:07 | 86:56 | 118.5933 | 117.8822
2001-01-18 13:08 | 134.84 | 2001-01-15 00:07 | 87:01 | 121.56 | 121.8522
2001-01-18 13:13 | 132.75 | 2001-01-15 00:07 | 87:06 | 125.4033 | 126.0489
2001-01-18 13:18 | 132.75 | 2001-01-15 00:07 | 87:11 | 131.1833 | 129.7922
2001-01-18 13:23 | 139.21 | 2001-01-15 00:07 | 87:16 | 132.79 | 132.0278
2001-01-18 13:28 | 136.99 | 2001-01-15 00:07 | 87:21 | 132.11 | 131.2178
2001-01-18 13:33 | 139.21 | 2001-01-15 00:07 | 87:26 | 128.7533 | 127.3578
2001-01-18 13:38 | 100.32 | 2001-01-15 00:07 | 87:31 | 121.21 | 120.5933
2001-01-18 13:43 | 98.87 | 2001-01-15 00:07 | 87:36 | 111.8167 | 112.1933
2001-01-18 13:48 | 99.59 | 2001-01-15 00:07 | 87:41 | 103.5533 | 105.8022
2001-01-18 13:53 | 103.27 | 2001-01-15 00:07 | 87:46 | 102.0367 | 102.7078
2001-01-18 13:58 | 96.02 | 2001-01-15 00:07 | 87:51 | 102.5333 | 102.9522
2001-01-18 14:03 | 95.31 | 2001-01-15 00:07 | 87:56 | 104.2867 | 104.2944
2001-01-18 14:08 | 98.15 | 2001-01-15 00:07 | 88:01 | 106.0633 | 107.1844
2001-01-18 14:13 | 104.02 | 2001-01-15 00:07 | 88:06 | 111.2033 | 111.4511
2001-01-18 14:18 | 104.78 | 2001-01-15 00:07 | 88:11 | 117.0867 | 116.61
2001-01-18 14:23 | 106.31 | 2001-01-15 00:07 | 88:16 | 121.54 | 118.5111
2001-01-18 14:28 | 105.54 | 2001-01-15 00:07 | 88:21 | 116.9067 | 115.4256
2001-01-18 14:33 | 98.87 | 2001-01-15 00:07 | 88:26 | 107.83 | 108.3722
2001-01-18 14:38 | 111.04 | 2001-01-15 00:07 | 88:31 | 100.38 | 102.3644
2001-01-18 14:43 | 118.57 | 2001-01-15 00:07 | 88:36 | 98.8833 | 100.7944
2001-01-18 14:48 | 104.02 | 2001-01-15 00:07 | 88:41 | 103.12 | 102.8822
2001-01-18 14:53 | 103.27 | 2001-01-15 00:07 | 88:46 | 106.6433 | 106.5789
2001-01-18 14:58 | 115.99 | 2001-01-15 00:07 | 88:51 | 109.9733 | 110.1722
2001-01-18 15:03 | 121.22 | 2001-01-15 00:07 | 88:56 | 113.9 | 116.1522
2001-01-18 15:08 | 118.57 | 2001-01-15 00:07 | 89:01 | 124.5833 | 123.0967
2001-01-18 15:13 | 124.89 | 2001-01-15 00:07 | 89:06 | 130.8067 | 130.3644
2001-01-18 15:18 | 132.75 | 2001-01-15 00:07 | 89:11 | 135.7033 | 133.8178
2001-01-18 15:23 | 135.91 | 2001-01-15 00:07 | 89:16 | 134.9433 | 135.1967
2001-01-18 15:28 | 129.71 | 2001-01-15 00:07 | 89:21 | 134.9433 | 130.3544
2001-01-18 15:33 | 130.71 | 2001-01-15 00:07 | 89:26 | 121.1767 | 121.6078
2001-01-18 15:38 | 125.84 | 2001-01-15 00:07 | 89:31 | 108.7033 | 110.0911
2001-01-18 15:43 | 107.08 | 2001-01-15 00:07 | 89:36 | 100.3933 | 104.7233
2001-01-18 15:48 | 102.53 | 2001-01-15 00:07 | 89:41 | 105.0733 | 104.4522
2001-01-18 15:53 | 101.05 | 2001-01-15 00:07 | 89:46 | 107.89 | 108.0111
2001-01-18 15:58 | 102.53 | 2001-01-15 00:07 | 89:51 | 111.07 | 111.4067
2001-01-18 16:03 | 104.02 | 2001-01-15 00:07 | 89:56 | 115.26 | 114.2244
2001-01-18 16:08 | 106.31 | 2001-01-15 00:07 | 90:01 | 116.3433 | 115.7989
2001-01-18 16:13 | 107.86 | 2001-01-15 00:07 | 90:06 | 115.7933 | 113.9
2001-01-18 16:18 | 119.44 | 2001-01-15 00:07 | 90:11 | 109.5633 | 111.3678
2001-01-18 16:23 | 123.96 | 2001-01-15 00:07 | 90:16 | 108.7467 | 108.3122
2001-01-18 16:28 | 121.22 | 2001-01-15 00:07 | 90:21 | 106.6267 | 107.3333
2001-01-18 16:33 | 105.54 | 2001-01-15 00:07 | 90:26 | 106.6267 | 106.0156
2001-01-18 16:38 | 96.73 | 2001-01-15 00:07 | 90:31 | 104.7933 | 105.3189
2001-01-18 16:43 | 98.87 | 2001-01-15 00:07 | 90:36 | 104.5367 | 105.0422
2001-01-18 16:48 | 101.05 | 2001-01-15 00:07 | 90:41 | 105.7967 | 105.81
2001-01-18 16:53 | 109.44 | 2001-01-15 00:07 | 90:46 | 107.0967 | 108.0144
2001-01-18 16:58 | 109.44 | 2001-01-15 00:07 | 90:51 | 111.15 | 110.9689
2001-01-18 17:03 | 111.04 | 2001-01-15 00:07 | 90:56 | 114.66 | 113.8489
2001-01-18 17:08 | 121.22 | 2001-01-15 00:07 | 91:01 | 115.7367 | 115.1878
2001-01-18 17:13 | 141.49 | 2001-01-15 00:07 | 91:06 | 115.1667 | 115.9433
2001-01-18 17:18 | 129.71 | 2001-01-15 00:07 | 91:11 | 116.9267 | 118.6867
2001-01-18 17:23 | 135.91 | 2001-01-15 00:07 | 91:16 | 123.9667 | 124.0756
2001-01-18 17:28 | 139.21 | 2001-01-15 00:07 | 91:21 | 131.3333 | 129.9444
2001-01-18 17:33 | 129.71 | 2001-01-15 00:07 | 91:26 | 134.5333 | 133.0133
2001-01-18 17:38 | 94.61 | 2001-01-15 00:07 | 91:31 | 133.1733 | 133.0333
2001-01-18 17:43 | 101.79 | 2001-01-15 00:07 | 91:36 | 131.3933 | 132.1011
2001-01-18 17:48 | 104.78 | 2001-01-15 00:07 | 91:41 | 131.7367 | 131.96
2001-01-18 17:53 | 108.65 | 2001-01-15 00:07 | 91:46 | 132.75 | 132.7633
2001-01-18 17:58 | 110.24 | 2001-01-15 00:07 | 91:51 | 133.8033 | 133.9233
2001-01-18 18:03 | 114.32 | 2001-01-15 00:07 | 91:56 | 135.2167 | 135.4633
2001-01-18 18:08 | 121.22 | 2001-01-15 00:07 | 92:01 | 137.37 | 134.5333
2001-01-18 18:13 | 113.49 | 2001-01-15 00:07 | 92:06 | 131.0133 | 130.2489
2001-01-18 18:18 | 112.67 | 2001-01-15 00:07 | 92:11 | 122.3633 | 122.4811
2001-01-18 18:23 | 102.53 | 2001-01-15 00:07 | 92:16 | 114.0667 | 116.01
2001-01-18 18:28 | 111.04 | 2001-01-15 00:07 | 92:21 | 111.6 | 112.2444
2001-01-18 18:33 | 106.31 | 2001-01-15 00:07 | 92:26 | 111.0667 | 111.0611
2001-01-18 18:38 | 102.53 | 2001-01-15 00:07 | 92:31 | 110.5167 | 111.6178
2001-01-18 18:43 | 105.54 | 2001-01-15 00:07 | 92:36 | 113.27 | 113.1744
2001-01-18 18:48 | 105.54 | 2001-01-15 00:07 | 92:41 | 115.7367 | 115.0978
2001-01-18 18:53 | 106.31 | 2001-01-15 00:07 | 92:46 | 116.2867 | 116.3956
2001-01-18 18:58 | 109.44 | 2001-01-15 00:07 | 92:51 | 117.1633 | 118.6389
2001-01-18 19:03 | 117.7 | 2001-01-15 00:07 | 92:56 | 122.4667 | 121.8733
2001-01-18 19:08 | 116.84 | 2001-01-15 00:07 | 93:01 | 125.99 | 123.43
2001-01-18 19:13 | 112.67 | 2001-01-15 00:07 | 93:06 | 121.8333 | 120.2811
2001-01-18 19:18 | 115.99 | 2001-01-15 00:07 | 93:11 | 113.02 | 113.8933
2001-01-18 19:23 | 122.12 | 2001-01-15 00:07 | 93:16 | 106.8267 | 108.8044
2001-01-18 19:28 | 133.79 | 2001-01-15 00:07 | 93:21 | 106.5667 | 106.9133
2001-01-18 19:33 | 138.09 | 2001-01-15 00:07 | 93:26 | 107.3467 | 107.7022
2001-01-18 19:38 | 131.72 | 2001-01-15 00:07 | 93:31 | 109.1933 | 109.5678
2001-01-18 19:43 | 129.71 | 2001-01-15 00:07 | 93:36 | 112.1633 | 112.7722
2001-01-18 19:48 | 132.75 | 2001-01-15 00:07 | 93:41 | 116.96 | 116.5022
2001-01-18 19:53 | 132.75 | 2001-01-15 00:07 | 93:46 | 120.3833 | 119.0567
2001-01-18 19:58 | 132.75 | 2001-01-15 00:07 | 93:51 | 119.8267 | 118.9511
2001-01-18 20:03 | 135.91 | 2001-01-15 00:07 | 93:56 | 116.6433 | 117.2133
2001-01-18 20:08 | 136.99 | 2001-01-15 00:07 | 94:01 | 115.17 | 115.3867
2001-01-18 20:13 | 139.21 | 2001-01-15 00:07 | 94:06 | 114.3467 | 114.53
2001-01-18 20:18 | 116.84 | 2001-01-15 00:07 | 94:11 | 114.0733 | 114.3578
2001-01-18 20:23 | 111.04 | 2001-01-15 00:07 | 94:16 | 114.6533 | 116.3356
2001-01-18 20:28 | 114.32 | 2001-01-15 00:07 | 94:21 | 120.28 | 120.6356
2001-01-18 20:33 | 109.44 | 2001-01-15 00:07 | 94:26 | 126.9733 | 124.8411
2001-01-18 20:38 | 109.44 | 2001-01-15 00:07 | 94:31 | 127.27 | 125.2956
2001-01-18 20:43 | 112.67 | 2001-01-15 00:07 | 94:36 | 121.6433 | 121.7511
2001-01-18 20:48 | 117.7 | 2001-01-15 00:07 | 94:41 | 116.34 | 117.8156
2001-01-18 20:53 | 116.84 | 2001-01-15 00:07 | 94:46 | 115.4633 | 115.6656
2001-01-18 20:58 | 114.32 | 2001-01-15 00:07 | 94:51 | 115.1933 | 115.0956
2001-01-18 21:03 | 120.33 | 2001-01-15 00:07 | 94:56 | 114.63 | 114.4422
2001-01-18 21:08 | 132.75 | 2001-01-15 00:07 | 95:01 | 113.5033 | 113.1833
2001-01-18 21:13 | 124.89 | 2001-01-15 00:07 | 95:06 | 111.4167 | 110.7922
2001-01-18 21:18 | 107.86 | 2001-01-15 00:07 | 95:11 | 107.4567 | 107.14
2001-01-18 21:23 | 106.31 | 2001-01-15 00:07 | 95:16 | 102.5467 | 103.2889
2001-01-18 21:28 | 106.31 | 2001-01-15 00:07 | 95:21 | 99.8633 | 99.7189
2001-01-18 21:33 | 107.08 | 2001-01-15 00:07 | 95:26 | 96.7467 | 97.0011
2001-01-18 21:38 | 108.65 | 2001-01-15 00:07 | 95:31 | 94.3933 | 94.4822
2001-01-18 21:43 | 111.85 | 2001-01-15 00:07 | 95:36 | 92.3067 | 92.3933
2001-01-18 21:48 | 115.99 | 2001-01-15 00:07 | 95:41 | 90.48 | 90.4856
2001-01-18 21:53 | 123.04 | 2001-01-15 00:07 | 95:46 | 88.67 | 88.7511
2001-01-18 21:58 | 122.12 | 2001-01-15 00:07 | 95:51 | 87.1033 | 87.2544
2001-01-18 22:03 | 114.32 | 2001-01-15 00:07 | 95:56 | 85.99 | 86.0667
2001-01-18 22:08 | 113.49 | 2001-01-15 00:07 | 96:01 | 85.1067 | 85.1811
2001-01-18 22:13 | 117.7 | 2001-01-15 00:07 | 96:06 | 84.4467 | 84.3756
2001-01-18 22:18 | 111.85 | 2001-01-15 00:07 | 96:11 | 83.5733 | 83.5022
2001-01-18 22:23 | 112.67 | 2001-01-15 00:07 | 96:16 | 82.4867 | 82.4167
2001-01-18 22:28 | 119.44 | 2001-01-15 00:07 | 96:21 | 81.19 | 81.1922
2001-01-18 22:33 | 128.73 | 2001-01-15 00:07 | 96:26 | 79.9 | 79.9722
2001-01-18 22:38 | 132.75 | 2001-01-15 00:07 | 96:31 | 78.8267 | 78.8978
2001-01-18 22:43 | 120.33 | 2001-01-15 00:07 | 96:36 | 77.9667 | 78.0389
2001-01-18 22:48 | 111.85 | 2001-01-15 00:07 | 96:41 | 77.3233 | 77.3222
2001-01-18 22:53 | 116.84 | 2001-01-15 00:07 | 96:46 | 76.6767 | 76.7489
2001-01-18 22:58 | 117.7 | 2001-01-15 00:07 | 96:51 | 76.2467 | 76.2467
2001-01-18 23:03 | 111.04 | 2001-01-15 00:07 | 96:56 | 75.8167 | 75.8889
2001-01-18 23:08 | 115.15 | 2001-01-15 00:07 | 97:01 | 75.6033 | 75.6033
2001-01-18 23:13 | 114.32 | 2001-01-15 00:07 | 97:06 | 75.39 | 75.4611
2001-01-18 23:18 | 104.78 | 2001-01-15 00:07 | 97:11 | 75.39 | 75.3178
2001-01-18 23:23 | 103.27 | 2001-01-15 00:07 | 97:16 | 75.1733 | 75.1733
2001-01-18 23:28 | 99.59 | 2001-01-15 00:07 | 97:21 | 74.9567 | 74.9567
2001-01-18 23:33 | 96.73 | 2001-01-15 00:07 | 97:26 | 74.74 | 74.7411
2001-01-18 23:38 | 93.92 | 2001-01-15 00:07 | 97:31 | 74.5267 | 74.5267
2001-01-18 23:43 | 92.53 | 2001-01-15 00:07 | 97:36 | 74.3133 | 74.3133
2001-01-18 23:48 | 90.47 | 2001-01-15 00:07 | 97:41 | 74.1 | 74.2422
2001-01-18 23:53 | 88.44 | 2001-01-15 00:07 | 97:46 | 74.3133 | 74.3133
2001-01-18 23:58 | 87.1 | 2001-01-15 00:07 | 97:51 | 74.5267 | 74.5267
2001-01-19 00:03 | 85.77 | 2001-01-15 00:07 | 97:56 | 74.74 | 74.7411
2001-01-19 00:08 | 85.1 | 2001-01-15 00:07 | 98:01 | 74.9567 | 74.9567
2001-01-19 00:13 | 84.45 | 2001-01-15 00:07 | 98:06 | 75.1733 | 75.1733
2001-01-19 00:18 | 83.79 | 2001-01-15 00:07 | 98:11 | 75.39 | 75.3178
2001-01-19 00:23 | 82.48 | 2001-01-15 00:07 | 98:16 | 75.39 | 75.3178
2001-01-19 00:28 | 81.19 | 2001-01-15 00:07 | 98:21 | 75.1733 | 75.1733
2001-01-19 00:33 | 79.9 | 2001-01-15 00:07 | 98:26 | 74.9567 | 74.9567
2001-01-19 00:38 | 78.61 | 2001-01-15 00:07 | 98:31 | 74.74 | 74.8122
2001-01-19 00:43 | 77.97 | 2001-01-15 00:07 | 98:36 | 74.74 | 74.74
2001-01-19 00:48 | 77.32 | 2001-01-15 00:07 | 98:41 | 74.74 | 74.74
2001-01-19 00:53 | 76.68 | 2001-01-15 00:07 | 98:46 | 74.74 | 74.74
2001-01-19 00:58 | 76.03 | 2001-01-15 00:07 | 98:51 | 74.74 | 74.74
2001-01-19 01:03 | 76.03 | 2001-01-15 00:07 | 98:56 | 74.74 | 74.6689
2001-01-19 01:08 | 75.39 | 2001-01-15 00:07 | 99:01 | 74.5267 | 74.5267
2001-01-19 01:13 | 75.39 | 2001-01-15 00:07 | 99:06 | 74.3133 | 74.3133
2001-01-19 01:18 | 75.39 | 2001-01-15 00:07 | 99:11 | 74.1 | 74.1011
2001-01-19 01:23 | 75.39 | 2001-01-15 00:07 | 99:16 | 73.89 | 73.89
2001-01-19 01:28 | 74.74 | 2001-01-15 00:07 | 99:21 | 73.68 | 73.68
2001-01-19 01:33 | 74.74 | 2001-01-15 00:07 | 99:26 | 73.47 | 73.54
2001-01-19 01:38 | 74.74 | 2001-01-15 00:07 | 99:31 | 73.47 | 73.54
2001-01-19 01:43 | 74.1 | 2001-01-15 00:07 | 99:36 | 73.68 | 73.68
2001-01-19 01:48 | 74.1 | 2001-01-15 00:07 | 99:41 | 73.89 | 73.82
2001-01-19 01:53 | 74.1 | 2001-01-15 00:07 | 99:46 | 73.89 | 73.82
2001-01-19 01:58 | 74.74 | 2001-01-15 00:07 | 99:51 | 73.68 | 73.6089
2001-01-19 02:03 | 74.74 | 2001-01-15 00:07 | 99:56 | 73.2567 | 73.3267
2001-01-19 02:08 | 74.74 | 2001-01-15 00:07 | 100:01 | 73.0433 | 73.0433
2001-01-19 02:13 | 75.39 | 2001-01-15 00:07 | 100:06 | 72.83 | 72.8311
2001-01-19 02:18 | 75.39 | 2001-01-15 00:07 | 100:11 | 72.62 | 72.62
2001-01-19 02:23 | 75.39 | 2001-01-15 00:07 | 100:16 | 72.41 | 72.41
2001-01-19 02:28 | 75.39 | 2001-01-15 00:07 | 100:21 | 72.2 | 72.27
2001-01-19 02:33 | 74.74 | 2001-01-15 00:07 | 100:26 | 72.2 | 72.2
2001-01-19 02:38 | 74.74 | 2001-01-15 00:07 | 100:31 | 72.2 | 72.2
2001-01-19 02:43 | 74.74 | 2001-01-15 00:07 | 100:36 | 72.2 | 72.2
2001-01-19 02:48 | 74.74 | 2001-01-15 00:07 | 100:41 | 72.2 | 72.27
2001-01-19 02:53 | 74.74 | 2001-01-15 00:07 | 100:46 | 72.41 | 72.4811
2001-01-19 02:58 | 74.74 | 2001-01-15 00:07 | 100:51 | 72.8333 | 72.8333
2001-01-19 03:03 | 74.74 | 2001-01-15 00:07 | 100:56 | 73.2567 | 73.1867
2001-01-19 03:08 | 74.74 | 2001-01-15 00:07 | 101:01 | 73.47 | 73.3989
2001-01-19 03:13 | 74.1 | 2001-01-15 00:07 | 101:06 | 73.47 | 73.47
2001-01-19 03:18 | 74.1 | 2001-01-15 00:07 | 101:11 | 73.47 | 73.47
2001-01-19 03:23 | 74.1 | 2001-01-15 00:07 | 101:16 | 73.47 | 73.47
2001-01-19 03:28 | 73.47 | 2001-01-15 00:07 | 101:21 | 73.47 | 73.47
2001-01-19 03:33 | 73.47 | 2001-01-15 00:07 | 101:26 | 73.47 | 73.47
2001-01-19 03:38 | 73.47 | 2001-01-15 00:07 | 101:31 | 73.47 | 73.47
2001-01-19 03:43 | 73.47 | 2001-01-15 00:07 | 101:36 | 73.47 | 73.47
2001-01-19 03:48 | 74.1 | 2001-01-15 00:07 | 101:41 | 73.47 | 73.47
2001-01-19 03:53 | 74.1 | 2001-01-15 00:07 | 101:46 | 73.47 | 73.47
2001-01-19 03:58 | 73.47 | 2001-01-15 00:07 | 101:51 | 73.47 | 73.47
2001-01-19 04:03 | 73.47 | 2001-01-15 00:07 | 101:56 | 73.47 | 73.47
2001-01-19 04:08 | 72.83 | 2001-01-15 00:07 | 102:01 | 73.47 | 73.54
2001-01-19 04:13 | 72.83 | 2001-01-15 00:07 | 102:06 | 73.68 | 73.68
2001-01-19 04:18 | 72.83 | 2001-01-15 00:07 | 102:11 | 73.89 | 73.89
2001-01-19 04:23 | 72.2 | 2001-01-15 00:07 | 102:16 | 74.1 | 74.03
2001-01-19 04:28 | 72.2 | 2001-01-15 00:07 | 102:21 | 74.1 | 74.03
2001-01-19 04:33 | 72.2 | 2001-01-15 00:07 | 102:26 | 73.89 | 73.89
2001-01-19 04:38 | 72.2 | 2001-01-15 00:07 | 102:31 | 73.68 | 74.6089
2001-01-19 04:43 | 72.2 | 2001-01-15 00:07 | 102:36 | 76.2567 | 78.14
2001-01-19 04:48 | 72.2 | 2001-01-15 00:07 | 102:41 | 84.4833 | 85.39
2001-01-19 04:53 | 72.2 | 2001-01-15 00:07 | 102:46 | 95.43 | 93.7544
2001-01-19 04:58 | 72.83 | 2001-01-15 00:07 | 102:51 | 101.35 | 99.8633
2001-01-19 05:03 | 73.47 | 2001-01-15 00:07 | 102:56 | 102.81 | 103.5889
2001-01-19 05:08 | 73.47 | 2001-01-15 00:07 | 103:01 | 106.6067 | 106.7033
2001-01-19 05:13 | 73.47 | 2001-01-15 00:07 | 103:06 | 110.6933 | 111.4078
2001-01-19 05:18 | 73.47 | 2001-01-15 00:07 | 103:11 | 116.9233 | 116.7511
2001-01-19 05:23 | 73.47 | 2001-01-15 00:07 | 103:16 | 122.6367 | 123.4056
2001-01-19 05:28 | 73.47 | 2001-01-15 00:07 | 103:21 | 130.6567 | 129.8578
2001-01-19 05:33 | 73.47 | 2001-01-15 00:07 | 103:26 | 136.28 | 134.1733
2001-01-19 05:38 | 73.47 | 2001-01-15 00:07 | 103:31 | 135.5833 | 133.8889
2001-01-19 05:43 | 73.47 | 2001-01-15 00:07 | 103:36 | 129.8033 | 130.69
2001-01-19 05:48 | 73.47 | 2001-01-15 00:07 | 103:41 | 126.6833 | 127.0611
2001-01-19 05:53 | 73.47 | 2001-01-15 00:07 | 103:46 | 124.6967 | 125.4556
2001-01-19 05:58 | 73.47 | 2001-01-15 00:07 | 103:51 | 124.9867 | 123.7611
2001-01-19 06:03 | 73.47 | 2001-01-15 00:07 | 103:56 | 121.6 | 122.0111
2001-01-19 06:08 | 73.47 | 2001-01-15 00:07 | 104:01 | 119.4467 | 121.0878
2001-01-19 06:13 | 73.47 | 2001-01-15 00:07 | 104:06 | 122.2167 | 122.8689
2001-01-19 06:18 | 74.1 | 2001-01-15 00:07 | 104:11 | 126.9433 | 126.3011
2001-01-19 06:23 | 74.1 | 2001-01-15 00:07 | 104:16 | 129.7433 | 128.4922
2001-01-19 06:28 | 74.1 | 2001-01-15 00:07 | 104:21 | 128.79 | 127.2456
2001-01-19 06:33 | 74.1 | 2001-01-15 00:07 | 104:26 | 123.2033 | 123.65
2001-01-19 06:38 | 73.47 | 2001-01-15 00:07 | 104:31 | 118.9567 | 119.4778
2001-01-19 06:43 | 73.47 | 2001-01-15 00:07 | 104:36 | 116.2733 | 117.0744
2001-01-19 06:48 | 81.83 | 2001-01-15 00:07 | 104:41 | 115.9933 | 115.0111
2001-01-19 06:53 | 98.15 | 2001-01-15 00:07 | 104:46 | 112.7667 | 112.2522
2001-01-19 06:58 | 106.31 | 2001-01-15 00:07 | 104:51 | 107.9967 | 109.4022
2001-01-19 07:03 | 99.59 | 2001-01-15 00:07 | 104:56 | 107.4433 | 108.99
2001-01-19 07:08 | 102.53 | 2001-01-15 00:07 | 105:01 | 111.53 | 112.2444
2001-01-19 07:13 | 117.7 | 2001-01-15 00:07 | 105:06 | 117.76 | 116.95
2001-01-19 07:18 | 111.85 | 2001-01-15 00:07 | 105:11 | 121.56 | 121.8689
2001-01-19 07:23 | 121.22 | 2001-01-15 00:07 | 105:16 | 126.2867 | 125.4367
2001-01-19 07:28 | 134.84 | 2001-01-15 00:07 | 105:21 | 128.4633 | 128.2733
2001-01-19 07:33 | 135.91 | 2001-01-15 00:07 | 105:26 | 130.07 | 131.0378
2001-01-19 07:38 | 138.09 | 2001-01-15 00:07 | 105:31 | 134.58 | 133.0767
2001-01-19 07:43 | 132.75 | 2001-01-15 00:07 | 105:36 | 134.58 | 135.0333
2001-01-19 07:48 | 118.57 | 2001-01-15 00:07 | 105:41 | 135.94 | 132.8022
2001-01-19 07:53 | 128.73 | 2001-01-15 00:07 | 105:46 | 127.8867 | 130.9
2001-01-19 07:58 | 126.79 | 2001-01-15 00:07 | 105:51 | 128.8733 | 127.8733
2001-01-19 08:03 | 119.44 | 2001-01-15 00:07 | 105:56 | 126.86 | 128.7122
2001-01-19 08:08 | 118.57 | 2001-01-15 00:07 | 106:01 | 130.4033 | 129.6811
2001-01-19 08:13 | 120.33 | 2001-01-15 00:07 | 106:06 | 131.78 | 131.43
2001-01-19 08:18 | 127.75 | 2001-01-15 00:07 | 106:11 | 132.1067 | 130.7167
2001-01-19 08:23 | 132.75 | 2001-01-15 00:07 | 106:16 | 128.2633 | 128.0311
2001-01-19 08:28 | 128.73 | 2001-01-15 00:07 | 106:21 | 123.7233 | 124.1078
2001-01-19 08:33 | 124.89 | 2001-01-15 00:07 | 106:26 | 120.3367 | 121.2678
2001-01-19 08:38 | 115.99 | 2001-01-15 00:07 | 106:31 | 119.7433 | 120.7756
2001-01-19 08:43 | 115.99 | 2001-01-15 00:07 | 106:36 | 122.2467 | 122.5411
2001-01-19 08:48 | 116.84 | 2001-01-15 00:07 | 106:41 | 125.6333 | 125.8689
2001-01-19 08:53 | 115.15 | 2001-01-15 00:07 | 106:46 | 129.7267 | 127.2333
2001-01-19 08:58 | 106.31 | 2001-01-15 00:07 | 106:51 | 126.34 | 125.4144
2001-01-19 09:03 | 102.53 | 2001-01-15 00:07 | 106:56 | 120.1767 | 120.39
2001-01-19 09:08 | 113.49 | 2001-01-15 00:07 | 107:01 | 114.6533 | 116.8889
2001-01-19 09:13 | 118.57 | 2001-01-15 00:07 | 107:06 | 115.8367 | 117.6056
2001-01-19 09:18 | 121.22 | 2001-01-15 00:07 | 107:11 | 122.3267 | 122.1189
2001-01-19 09:23 | 124.89 | 2001-01-15 00:07 | 107:16 | 128.1933 | 125.0067
2001-01-19 09:28 | 132.75 | 2001-01-15 00:07 | 107:21 | 124.5 | 123.9289
2001-01-19 09:33 | 127.75 | 2001-01-15 00:07 | 107:26 | 119.0933 | 119.1278
2001-01-19 09:38 | 129.71 | 2001-01-15 00:07 | 107:31 | 113.79 | 116.3944
2001-01-19 09:43 | 146.28 | 2001-01-15 00:07 | 107:36 | 116.3 | 115.9311
2001-01-19 09:48 | 127.75 | 2001-01-15 00:07 | 107:41 | 117.7033 | 119.2356
2001-01-19 09:53 | 133.79 | 2001-01-15 00:07 | 107:46 | 123.7033 | 123.5111
2001-01-19 09:58 | 122.12 | 2001-01-15 00:07 | 107:51 | 129.1267 | 130.0922
2001-01-19 10:03 | 130.71 | 2001-01-15 00:07 | 107:56 | 137.4467 | 135.2844
2001-01-19 10:08 | 127.75 | 2001-01-15 00:07 | 108:01 | 139.28 | 136.0244
2001-01-19 10:13 | 132.75 | 2001-01-15 00:07 | 108:06 | 131.3467 | 128.73
2001-01-19 10:18 | 134.84 | 2001-01-15 00:07 | 108:11 | 115.5633 | 116.2167
2001-01-19 10:23 | 128.73 | 2001-01-15 00:07 | 108:16 | 101.74 | 105.2378
2001-01-19 10:28 | 121.22 | 2001-01-15 00:07 | 108:21 | 98.41 | 100.5722
2001-01-19 10:33 | 121.22 | 2001-01-15 00:07 | 108:26 | 101.5667 | 101.1711
2001-01-19 10:38 | 118.57 | 2001-01-15 00:07 | 108:31 | 103.5367 | 102.5578
2001-01-19 10:43 | 119.44 | 2001-01-15 00:07 | 108:36 | 102.57 | 101.1522
2001-01-19 10:48 | 128.73 | 2001-01-15 00:07 | 108:41 | 97.35 | 98.2744
2001-01-19 10:53 | 128.73 | 2001-01-15 00:07 | 108:46 | 94.9033 | 98.4844
2001-01-19 10:58 | 131.72 | 2001-01-15 00:07 | 108:51 | 103.2 | 105.8756
2001-01-19 11:03 | 118.57 | 2001-01-15 00:07 | 108:56 | 119.5233 | 117.45
2001-01-19 11:08 | 110.24 | 2001-01-15 00:07 | 109:01 | 129.6267 | 126.0567
2001-01-19 11:13 | 115.15 | 2001-01-15 00:07 | 109:06 | 129.02 | 127.6522
2001-01-19 11:18 | 122.12 | 2001-01-15 00:07 | 109:11 | 124.31 | 126.2089
2001-01-19 11:23 | 129.71 | 2001-01-15 00:07 | 109:16 | 125.2967 | 127.4822
2001-01-19 11:28 | 132.75 | 2001-01-15 00:07 | 109:21 | 132.84 | 132.4033
2001-01-19 11:33 | 111.04 | 2001-01-15 00:07 | 109:26 | 139.0733 | 134.1989
2001-01-19 11:38 | 113.49 | 2001-01-15 00:07 | 109:31 | 130.6833 | 128.1656
2001-01-19 11:43 | 116.84 | 2001-01-15 00:07 | 109:36 | 114.74 | 115.4311
2001-01-19 11:48 | 118.57 | 2001-01-15 00:07 | 109:41 | 100.87 | 104.6722
2001-01-19 11:53 | 117.7 | 2001-01-15 00:07 | 109:46 | 98.4067 | 100.1167
2001-01-19 11:58 | 134.84 | 2001-01-15 00:07 | 109:51 | 101.0733 | 100.9411
2001-01-19 12:03 | 134.84 | 2001-01-15 00:07 | 109:56 | 103.3433 | 103.93
2001-01-19 12:08 | 142.66 | 2001-01-15 00:07 | 110:01 | 107.3733 | 106.9911
2001-01-19 12:13 | 140.34 | 2001-01-15 00:07 | 110:06 | 110.2567 | 109.83
2001-01-19 12:18 | 111.04 | 2001-01-15 00:07 | 110:11 | 111.86 | 111.1489
2001-01-19 12:23 | 95.31 | 2001-01-15 00:07 | 110:16 | 111.33 | 111.8756
2001-01-19 12:28 | 98.87 | 2001-01-15 00:07 | 110:21 | 112.4367 | 111.6211
2001-01-19 12:33 | 101.05 | 2001-01-15 00:07 | 110:26 | 111.0967 | 111.8089
2001-01-19 12:38 | 104.78 | 2001-01-15 00:07 | 110:31 | 111.8933 | 111.1678
2001-01-19 12:43 | 104.78 | 2001-01-15 00:07 | 110:36 | 110.5133 | 111.6956
2001-01-19 12:48 | 98.15 | 2001-01-15 00:07 | 110:41 | 112.68 | 111.3467
2001-01-19 12:53 | 89.12 | 2001-01-15 00:07 | 110:46 | 110.8467 | 111.4578
2001-01-19 12:58 | 97.44 | 2001-01-15 00:07 | 110:51 | 110.8467 | 111.7233
2001-01-19 13:03 | 123.04 | 2001-01-15 00:07 | 110:56 | 113.4767 | 115.6233
2001-01-19 13:08 | 138.09 | 2001-01-15 00:07 | 111:01 | 122.5467 | 122.5633
2001-01-19 13:13 | 127.75 | 2001-01-15 00:07 | 111:06 | 131.6667 | 130.5489
2001-01-19 13:18 | 121.22 | 2001-01-15 00:07 | 111:11 | 137.4333 | 136.1044
2001-01-19 13:23 | 123.96 | 2001-01-15 00:07 | 111:16 | 139.2133 | 137.4556
2001-01-19 13:28 | 130.71 | 2001-01-15 00:07 | 111:21 | 135.72 | 133.54
2001-01-19 13:33 | 143.85 | 2001-01-15 00:07 | 111:26 | 125.6867 | 124.6733
2001-01-19 13:38 | 142.66 | 2001-01-15 00:07 | 111:31 | 112.6133 | 113.1033
2001-01-19 13:43 | 105.54 | 2001-01-15 00:07 | 111:36 | 101.01 | 102.7578
2001-01-19 13:48 | 96.02 | 2001-01-15 00:07 | 111:41 | 94.65 | 95.7611
2001-01-19 13:53 | 101.05 | 2001-01-15 00:07 | 111:46 | 91.6233 | 93.4244
2001-01-19 13:58 | 98.15 | 2001-01-15 00:07 | 111:51 | 94 | 96.0611
2001-01-19 14:03 | 104.02 | 2001-01-15 00:07 | 111:56 | 102.56 | 103.7122
2001-01-19 14:08 | 107.86 | 2001-01-15 00:07 | 112:01 | 114.5767 | 112.0456
2001-01-19 14:13 | 110.24 | 2001-01-15 00:07 | 112:06 | 119 | 116.5278
2001-01-19 14:18 | 112.67 | 2001-01-15 00:07 | 112:11 | 116.0067 | 115.5411
2001-01-19 14:23 | 112.67 | 2001-01-15 00:07 | 112:16 | 111.6167 | 113.2656
2001-01-19 14:28 | 108.65 | 2001-01-15 00:07 | 112:21 | 112.1733 | 112.7978
2001-01-19 14:33 | 115.99 | 2001-01-15 00:07 | 112:26 | 114.6033 | 114.8433
2001-01-19 14:38 | 108.65 | 2001-01-15 00:07 | 112:31 | 117.7533 | 115.8
2001-01-19 14:43 | 111.04 | 2001-01-15 00:07 | 112:36 | 115.0433 | 114.38
2001-01-19 14:48 | 111.85 | 2001-01-15 00:07 | 112:41 | 110.3433 | 107.5778
2001-01-19 14:53 | 115.15 | 2001-01-15 00:07 | 112:46 | 97.3467 | 99.15
2001-01-19 14:58 | 105.54 | 2001-01-15 00:07 | 112:51 | 89.76 | 90.8878
2001-01-19 15:03 | 111.85 | 2001-01-15 00:07 | 112:56 | 85.5567 | 89.1956
2001-01-19 15:08 | 123.04 | 2001-01-15 00:07 | 113:01 | 92.27 | 92.4744
2001-01-19 15:13 | 132.75 | 2001-01-15 00:07 | 113:06 | 99.5967 | 99.5767
2001-01-19 15:18 | 139.21 | 2001-01-15 00:07 | 113:11 | 106.8633 | 104.6089
2001-01-19 15:23 | 140.34 | 2001-01-15 00:07 | 113:16 | 107.3667 | 106.9433
2001-01-19 15:28 | 138.09 | 2001-01-15 00:07 | 113:21 | 106.6 | 106.3333
2001-01-19 15:33 | 128.73 | 2001-01-15 00:07 | 113:26 | 105.0333 | 105.8978
2001-01-19 15:38 | 110.24 | 2001-01-15 00:07 | 113:31 | 106.06 | 106.7778
2001-01-19 15:43 | 98.87 | 2001-01-15 00:07 | 113:36 | 109.24 | 109.5311
2001-01-19 15:48 | 93.92 | 2001-01-15 00:07 | 113:41 | 113.2933 | 113.2289
2001-01-19 15:53 | 91.16 | 2001-01-15 00:07 | 113:46 | 117.1533 | 116.6333
2001-01-19 15:58 | 89.79 | 2001-01-15 00:07 | 113:51 | 119.4533 | 118.2189
2001-01-19 16:03 | 101.05 | 2001-01-15 00:07 | 113:56 | 118.05 | 118.3244
2001-01-19 16:08 | 116.84 | 2001-01-15 00:07 | 114:01 | 117.47 | 117.7633
2001-01-19 16:13 | 125.84 | 2001-01-15 00:07 | 114:06 | 117.77 | 119.3633
2001-01-19 16:18 | 114.32 | 2001-01-15 00:07 | 114:11 | 122.85 | 123.0611
2001-01-19 16:23 | 107.86 | 2001-01-15 00:07 | 114:16 | 128.5633 | 128.9411
2001-01-19 16:28 | 112.67 | 2001-01-15 00:07 | 114:21 | 135.41 | 134.1678
2001-01-19 16:33 | 115.99 | 2001-01-15 00:07 | 114:26 | 138.53 | 137.7289
2001-01-19 16:38 | 115.15 | 2001-01-15 00:07 | 114:31 | 139.2467 | 136.4278
2001-01-19 16:43 | 122.12 | 2001-01-15 00:07 | 114:36 | 131.5067 | 130.9922
2001-01-19 16:48 | 107.86 | 2001-01-15 00:07 | 114:41 | 122.2233 | 123.5656
2001-01-19 16:53 | 101.05 | 2001-01-15 00:07 | 114:46 | 116.9667 | 118.6222
2001-01-19 16:58 | 83.13 | 2001-01-15 00:07 | 114:51 | 116.6767 | 117.4122
2001-01-19 17:03 | 85.1 | 2001-01-15 00:07 | 114:56 | 118.5933 | 116.8233
2001-01-19 17:08 | 88.44 | 2001-01-15 00:07 | 115:01 | 115.2 | 115.8589
2001-01-19 17:13 | 103.27 | 2001-01-15 00:07 | 115:06 | 113.7833 | 115.8911
2001-01-19 17:18 | 107.08 | 2001-01-15 00:07 | 115:11 | 118.69 | 119.9378
2001-01-19 17:23 | 110.24 | 2001-01-15 00:07 | 115:16 | 127.34 | 126.62
2001-01-19 17:28 | 104.78 | 2001-01-15 00:07 | 115:21 | 133.83 | 129.5711
2001-01-19 17:33 | 104.78 | 2001-01-15 00:07 | 115:26 | 127.5433 | 125.8922
2001-01-19 17:38 | 105.54 | 2001-01-15 00:07 | 115:31 | 116.3033 | 117.3444
2001-01-19 17:43 | 107.86 | 2001-01-15 00:07 | 115:36 | 108.1867 | 110.4489
2001-01-19 17:48 | 114.32 | 2001-01-15 00:07 | 115:41 | 106.8567 | 107.81
2001-01-19 17:53 | 117.7 | 2001-01-15 00:07 | 115:46 | 108.3867 | 107.7011
2001-01-19 17:58 | 119.44 | 2001-01-15 00:07 | 115:51 | 107.86 | 108.2111
2001-01-19 18:03 | 121.22 | 2001-01-15 00:07 | 115:56 | 108.3867 | 109.4978
2001-01-19 18:08 | 113.49 | 2001-01-15 00:07 | 116:01 | 112.2467 | 113.8411
2001-01-19 18:13 | 117.7 | 2001-01-15 00:07 | 116:06 | 120.89 | 121.1922
2001-01-19 18:18 | 122.12 | 2001-01-15 00:07 | 116:11 | 130.44 | 129.2067
2001-01-19 18:23 | 128.73 | 2001-01-15 00:07 | 116:16 | 136.29 | 131.9933
2001-01-19 18:28 | 134.84 | 2001-01-15 00:07 | 116:21 | 129.25 | 127.98
2001-01-19 18:33 | 142.66 | 2001-01-15 00:07 | 116:26 | 118.4 | 118.4378
2001-01-19 18:38 | 138.09 | 2001-01-15 00:07 | 116:31 | 107.6633 | 110.5356
2001-01-19 18:43 | 136.99 | 2001-01-15 00:07 | 116:36 | 105.5433 | 106.4211
2001-01-19 18:48 | 119.44 | 2001-01-15 00:07 | 116:41 | 106.0567 | 106.2278
2001-01-19 18:53 | 110.24 | 2001-01-15 00:07 | 116:46 | 107.0833 | 107.0889
2001-01-19 18:58 | 121.22 | 2001-01-15 00:07 | 116:51 | 108.1267 | 108.7689
2001-01-19 19:03 | 118.57 | 2001-01-15 00:07 | 116:56 | 111.0967 | 111.4922
2001-01-19 19:08 | 115.99 | 2001-01-15 00:07 | 117:01 | 115.2533 | 116.2311
2001-01-19 19:13 | 111.04 | 2001-01-15 00:07 | 117:06 | 122.3433 | 121.0744
2001-01-19 19:18 | 114.32 | 2001-01-15 00:07 | 117:11 | 125.6267 | 125.6856
2001-01-19 19:23 | 130.71 | 2001-01-15 00:07 | 117:16 | 129.0867 | 127.0811
2001-01-19 19:28 | 136.99 | 2001-01-15 00:07 | 117:21 | 126.53 | 127.0711
2001-01-19 19:33 | 133.79 | 2001-01-15 00:07 | 117:26 | 125.5967 | 125.5789
2001-01-19 19:38 | 111.85 | 2001-01-15 00:07 | 117:31 | 124.61 | 125.4622
2001-01-19 19:43 | 103.27 | 2001-01-15 00:07 | 117:36 | 126.18 | 124.5044
2001-01-19 19:48 | 109.44 | 2001-01-15 00:07 | 117:41 | 122.7233 | 123.15
2001-01-19 19:53 | 107.86 | 2001-01-15 00:07 | 117:46 | 120.5467 | 121.06
2001-01-19 19:58 | 107.86 | 2001-01-15 00:07 | 117:51 | 119.91 | 121.48
2001-01-19 20:03 | 107.86 | 2001-01-15 00:07 | 117:56 | 123.9833 | 122.8278
2001-01-19 20:08 | 109.44 | 2001-01-15 00:07 | 118:01 | 124.59 | 125.7489
2001-01-19 20:13 | 119.44 | 2001-01-15 00:07 | 118:06 | 128.6733 | 126.5133
2001-01-19 20:18 | 133.79 | 2001-01-15 00:07 | 118:11 | 126.2767 | 126.3867
2001-01-19 20:23 | 138.09 | 2001-01-15 00:07 | 118:16 | 124.21 | 123.3289
2001-01-19 20:28 | 136.99 | 2001-01-15 00:07 | 118:21 | 119.5 | 122.2956
2001-01-19 20:33 | 112.67 | 2001-01-15 00:07 | 118:26 | 123.1767 | 123.4922
2001-01-19 20:38 | 105.54 | 2001-01-15 00:07 | 118:31 | 127.8 | 127.5867
2001-01-19 20:43 | 104.78 | 2001-01-15 00:07 | 118:36 | 131.7833 | 131.62
2001-01-19 20:48 | 106.31 | 2001-01-15 00:07 | 118:41 | 135.2767 | 134.5711
2001-01-19 20:53 | 107.08 | 2001-01-15 00:07 | 118:46 | 136.6533 | 136.5611
2001-01-19 20:58 | 107.86 | 2001-01-15 00:07 | 118:51 | 137.7533 | 137.14
2001-01-19 21:03 | 109.44 | 2001-01-15 00:07 | 118:56 | 137.0133 | 137.26
2001-01-19 21:08 | 115.99 | 2001-01-15 00:07 | 119:01 | 137.0133 | 136.5278
2001-01-19 21:13 | 120.33 | 2001-01-15 00:07 | 119:06 | 135.5567 | 135.8033
2001-01-19 21:18 | 130.71 | 2001-01-15 00:07 | 119:11 | 134.84 | 135.0789
2001-01-19 21:23 | 125.84 | 2001-01-15 00:07 | 119:16 | 134.84 | 134.3811
2001-01-19 21:28 | 130.71 | 2001-01-15 00:07 | 119:21 | 133.4633 | 134.1611
2001-01-19 21:33 | 123.04 | 2001-01-15 00:07 | 119:26 | 134.18 | 134.06
2001-01-19 21:38 | 123.04 | 2001-01-15 00:07 | 119:31 | 134.5367 | 134.9956
2001-01-19 21:43 | 127.75 | 2001-01-15 00:07 | 119:36 | 136.27 | 135.3367
2001-01-19 21:48 | 127.75 | 2001-01-15 00:07 | 119:41 | 135.2033 | 135.2078
2001-01-19 21:53 | 112.67 | 2001-01-15 00:07 | 119:46 | 134.15 | 134.3822
2001-01-19 21:58 | 121.22 | 2001-01-15 00:07 | 119:51 | 133.7933 | 133.9122
2001-01-19 22:03 | 125.84 | 2001-01-15 00:07 | 119:56 | 133.7933 | 132.7144
2001-01-19 22:08 | 124.89 | 2001-01-15 00:07 | 120:01 | 130.5567 | 131.0656
2001-01-19 22:13 | 123.04 | 2001-01-15 00:07 | 120:06 | 128.8467 | 127.2533
2001-01-19 22:18 | 138.09 | 2001-01-15 00:07 | 120:11 | 122.3567 | 125.2611
2001-01-19 22:23 | 117.7 | 2001-01-15 00:07 | 120:16 | 124.58 | 124.8944
2001-01-19 22:28 | 116.84 | 2001-01-15 00:07 | 120:21 | 127.7467 | 129.21
2001-01-19 22:33 | 123.96 | 2001-01-15 00:07 | 120:26 | 135.3033 | 133.3544
2001-01-19 22:38 | 128.73 | 2001-01-15 00:07 | 120:31 | 137.0133 | 135.7256
2001-01-19 22:43 | 130.71 | 2001-01-15 00:07 | 120:36 | 134.86 | 135.3389
2001-01-19 22:48 | 135.91 | 2001-01-15 00:07 | 120:41 | 134.1433 | 134.5011
2001-01-19 22:53 | 139.21 | 2001-01-15 00:07 | 120:46 | 134.5 | 133.7189
2001-01-19 22:58 | 134.84 | 2001-01-15 00:07 | 120:51 | 132.5133 | 130.8033
2001-01-19 23:03 | 139.21 | 2001-01-15 00:07 | 120:56 | 125.3967 | 125.8422
2001-01-19 23:08 | 136.99 | 2001-01-15 00:07 | 121:01 | 119.6167 | 120.9244
2001-01-19 23:13 | 134.84 | 2001-01-15 00:07 | 121:06 | 117.76 | 121.2367
2001-01-19 23:18 | 134.84 | 2001-01-15 00:07 | 121:11 | 126.3333 | 125.2833
2001-01-19 23:23 | 134.84 | 2001-01-15 00:07 | 121:16 | 131.7567 | 131.5811
2001-01-19 23:28 | 134.84 | 2001-01-15 00:07 | 121:21 | 136.6533 | 134.7744
2001-01-19 23:33 | 130.71 | 2001-01-15 00:07 | 121:26 | 135.9133 | 135.7011
2001-01-19 23:38 | 136.99 | 2001-01-15 00:07 | 121:31 | 134.5367 | 134.9956
2001-01-19 23:43 | 135.91 | 2001-01-15 00:07 | 121:36 | 134.5367 | 134.1811
2001-01-19 23:48 | 135.91 | 2001-01-15 00:07 | 121:41 | 133.47 | 132.0044
2001-01-19 23:53 | 133.79 | 2001-01-15 00:07 | 121:46 | 128.0067 | 127.8044
2001-01-19 23:58 | 132.75 | 2001-01-15 00:07 | 121:51 | 121.9367 | 122.2689
2001-01-20 00:03 | 134.84 | 2001-01-15 00:07 | 121:56 | 116.8633 | 118.93
2001-01-20 00:08 | 133.79 | 2001-01-15 00:07 | 122:01 | 117.99 | 116.3489
2001-01-20 00:13 | 123.04 | 2001-01-15 00:07 | 122:06 | 114.1933 | 112.9533
2001-01-20 00:18 | 129.71 | 2001-01-15 00:07 | 122:11 | 106.6767 | 106.2333
2001-01-20 00:23 | 114.32 | 2001-01-15 00:07 | 122:16 | 97.83 | 98.7933
2001-01-20 00:28 | 129.71 | 2001-01-15 00:07 | 122:21 | 91.8733 | 92.8678
2001-01-20 00:33 | 139.21 | 2001-01-15 00:07 | 122:26 | 88.9 | 89.2178
2001-01-20 00:38 | 136.99 | 2001-01-15 00:07 | 122:31 | 86.88 | 87.11
2001-01-20 00:43 | 134.84 | 2001-01-15 00:07 | 122:36 | 85.55 | 85.6256
2001-01-20 00:48 | 132.75 | 2001-01-15 00:07 | 122:41 | 84.4467 | 84.5956
2001-01-20 00:53 | 134.84 | 2001-01-15 00:07 | 122:46 | 83.79 | 83.79
2001-01-20 00:58 | 135.91 | 2001-01-15 00:07 | 122:51 | 83.1333 | 83.2067
2001-01-20 01:03 | 126.79 | 2001-01-15 00:07 | 122:56 | 82.6967 | 82.6978
2001-01-20 01:08 | 113.49 | 2001-01-15 00:07 | 123:01 | 82.2633 | 82.2644
2001-01-20 01:13 | 118.57 | 2001-01-15 00:07 | 123:06 | 81.8333 | 81.8333
2001-01-20 01:18 | 121.22 | 2001-01-15 00:07 | 123:11 | 81.4033 | 81.4756
2001-01-20 01:23 | 139.21 | 2001-01-15 00:07 | 123:16 | 81.19 | 81.1889
2001-01-20 01:28 | 134.84 | 2001-01-15 00:07 | 123:21 | 80.9733 | 80.9733
2001-01-20 01:33 | 135.91 | 2001-01-15 00:07 | 123:26 | 80.7567 | 80.6856
2001-01-20 01:38 | 136.99 | 2001-01-15 00:07 | 123:31 | 80.3267 | 80.3989
2001-01-20 01:43 | 130.71 | 2001-01-15 00:07 | 123:36 | 80.1133 | 80.1133
2001-01-20 01:48 | 135.91 | 2001-01-15 00:07 | 123:41 | 79.9 | 79.8989
2001-01-20 01:53 | 133.79 | 2001-01-15 00:07 | 123:46 | 79.6833 | 79.6833
2001-01-20 01:58 | 114.32 | 2001-01-15 00:07 | 123:51 | 79.4667 | 79.4667
2001-01-20 02:03 | 117.7 | 2001-01-15 00:07 | 123:56 | 79.25 | 79.2511
2001-01-20 02:08 | 118.57 | 2001-01-15 00:07 | 124:01 | 79.0367 | 79.0367
2001-01-20 02:13 | 117.7 | 2001-01-15 00:07 | 124:06 | 78.8233 | 78.8233
2001-01-20 02:18 | 106.31 | 2001-01-15 00:07 | 124:11 | 78.61 | 78.6811
2001-01-20 02:23 | 96.02 | 2001-01-15 00:07 | 124:16 | 78.61 | 78.61
2001-01-20 02:28 | 91.16 | 2001-01-15 00:07 | 124:21 | 78.61 | 78.61
2001-01-20 02:33 | 88.44 | 2001-01-15 00:07 | 124:26 | 78.61 | 78.5389
2001-01-20 02:38 | 87.1 | 2001-01-15 00:07 | 124:31 | 78.3967 | 78.3967
2001-01-20 02:43 | 85.1 | 2001-01-15 00:07 | 124:36 | 78.1833 | 78.1833
2001-01-20 02:48 | 84.45 | 2001-01-15 00:07 | 124:41 | 77.97 | 78.0411
2001-01-20 02:53 | 83.79 | 2001-01-15 00:07 | 124:46 | 77.97 | 77.97
2001-01-20 02:58 | 83.13 | 2001-01-15 00:07 | 124:51 | 77.97 | 77.97
2001-01-20 03:03 | 82.48 | 2001-01-15 00:07 | 124:56 | 77.97 | 77.97
2001-01-20 03:08 | 82.48 | 2001-01-15 00:07 | 125:01 | 77.97 | 77.8978
2001-01-20 03:13 | 81.83 | 2001-01-15 00:07 | 125:06 | 77.7533 | 77.7533
2001-01-20 03:18 | 81.19 | 2001-01-15 00:07 | 125:11 | 77.5367 | 77.5367
2001-01-20 03:23 | 81.19 | 2001-01-15 00:07 | 125:16 | 77.32 | 77.3211
2001-01-20 03:28 | 81.19 | 2001-01-15 00:07 | 125:21 | 77.1067 | 77.1778
2001-01-20 03:33 | 80.54 | 2001-01-15 00:07 | 125:26 | 77.1067 | 77.1067
2001-01-20 03:38 | 80.54 | 2001-01-15 00:07 | 125:31 | 77.1067 | 77.1778
2001-01-20 03:43 | 79.9 | 2001-01-15 00:07 | 125:36 | 77.32 | 77.2489
2001-01-20 03:48 | 79.9 | 2001-01-15 00:07 | 125:41 | 77.32 | 77.32
2001-01-20 03:53 | 79.9 | 2001-01-15 00:07 | 125:46 | 77.32 | 77.32
2001-01-20 03:58 | 79.25 | 2001-01-15 00:07 | 125:51 | 77.32 | 77.32
2001-01-20 04:03 | 79.25 | 2001-01-15 00:07 | 125:56 | 77.32 | 77.2489
2001-01-20 04:08 | 79.25 | 2001-01-15 00:07 | 126:01 | 77.1067 | 77.1067
2001-01-20 04:13 | 78.61 | 2001-01-15 00:07 | 126:06 | 76.8933 | 76.8933
2001-01-20 04:18 | 78.61 | 2001-01-15 00:07 | 126:11 | 76.68 | 76.7511
2001-01-20 04:23 | 78.61 | 2001-01-15 00:07 | 126:16 | 76.68 | 76.68
2001-01-20 04:28 | 78.61 | 2001-01-15 00:07 | 126:21 | 76.68 | 81.0478
2001-01-20 04:33 | 78.61 | 2001-01-15 00:07 | 126:26 | 89.7833 | 91.8778
2001-01-20 04:38 | 78.61 | 2001-01-15 00:07 | 126:31 | 109.17 | 108.9378
2001-01-20 04:43 | 77.97 | 2001-01-15 00:07 | 126:36 | 127.86 | 123.2656
2001-01-20 04:48 | 77.97 | 2001-01-15 00:07 | 126:41 | 132.7667 | 130.6722
2001-01-20 04:53 | 77.97 | 2001-01-15 00:07 | 126:46 | 131.39 | 131.4022
2001-01-20 04:58 | 77.97 | 2001-01-15 00:07 | 126:51 | 130.05 | 127.9578
2001-01-20 05:03 | 77.97 | 2001-01-15 00:07 | 126:56 | 122.4333 | 123.3367
2001-01-20 05:08 | 77.97 | 2001-01-15 00:07 | 127:01 | 117.5267 | 119.0533
2001-01-20 05:13 | 77.97 | 2001-01-15 00:07 | 127:06 | 117.2 | 118.4989
2001-01-20 05:18 | 77.32 | 2001-01-15 00:07 | 127:11 | 120.77 | 120.5689
2001-01-20 05:23 | 77.32 | 2001-01-15 00:07 | 127:16 | 123.7367 | 120.8911
2001-01-20 05:28 | 77.32 | 2001-01-15 00:07 | 127:21 | 118.1667 | 116.9011
2001-01-20 05:33 | 76.68 | 2001-01-15 00:07 | 127:26 | 108.8 | 109.52
2001-01-20 05:38 | 77.32 | 2001-01-15 00:07 | 127:31 | 101.5933 | 107.5089
2001-01-20 05:43 | 77.32 | 2001-01-15 00:07 | 127:36 | 112.1333 | 111.55
2001-01-20 05:48 | 77.32 | 2001-01-15 00:07 | 127:41 | 120.9233 | 118.9467
2001-01-20 05:53 | 77.32 | 2001-01-15 00:07 | 127:46 | 123.7833 | 119.5889
2001-01-20 05:58 | 77.32 | 2001-01-15 00:07 | 127:51 | 114.06 | 117.1133
2001-01-20 06:03 | 77.32 | 2001-01-15 00:07 | 127:56 | 113.4967 | 113.9589
2001-01-20 06:08 | 77.32 | 2001-01-15 00:07 | 128:01 | 114.32 | 113.9083
2001-01-20 06:13 | 76.68 | 2001-01-15 00:07
2001-01-20 06:18 | 76.68 | 2001-01-15 00:07
2001-01-20 06:23 | 76.68 | 2001-01-15 00:07
2001-01-20 06:28 | 76.68 | 2001-01-15 00:07
2001-01-20 06:33 | 76.68 | 2001-01-15 00:07
2001-01-20 06:38 | 115.99 | 2001-01-15 00:07
2001-01-20 06:43 | 134.84 | 2001-01-15 00:07
2001-01-20 06:48 | 132.75 | 2001-01-15 00:07
2001-01-20 06:53 | 130.71 | 2001-01-15 00:07
2001-01-20 06:58 | 130.71 | 2001-01-15 00:07
2001-01-20 07:03 | 128.73 | 2001-01-15 00:07
2001-01-20 07:08 | 107.86 | 2001-01-15 00:07
2001-01-20 07:13 | 115.99 | 2001-01-15 00:07
2001-01-20 07:18 | 127.75 | 2001-01-15 00:07
2001-01-20 07:23 | 118.57 | 2001-01-15 00:07
2001-01-20 07:28 | 124.89 | 2001-01-15 00:07
2001-01-20 07:33 | 111.04 | 2001-01-15 00:07
2001-01-20 07:38 | 90.47 | 2001-01-15 00:07
2001-01-20 07:43 | 103.27 | 2001-01-15 00:07
2001-01-20 07:48 | 142.66 | 2001-01-15 00:07
2001-01-20 07:53 | 116.84 | 2001-01-15 00:07
2001-01-20 07:58 | 111.85 | 2001-01-15 00:07
2001-01-20 08:03 | 113.49 | 2001-01-15 00:07
2001-01-20 08:08 | 115.15 | 2001-01-15 00:07